## ToDo&Log
1. 수정이력 | Version | 내용 | Sheet | 이유 | PC | Main | IOM | MMI
1) 2024-4-23 | V0.01 | MIN/MAX 개별 TimeStamp 추가 - 그에 따라 이후 데이터 address 변경 | modbus | 기존에는 개별 시간이 없이 공통 시간만 있음 | O | O |  | O
|  | IOM-SOE 기능, Setting Enable 추가 | IOM |  |  | O | O
|  | IOM - Timestamp 12byte->8 byte | IOM |  |  | O | O
2) 2024-4-24 | V0.02 | Meter IO 내용 변경(addr 250) | modbus | io영역 중 일부 복사 | ? | O |  | ? | 읽어가는 영역에 따라
3) 2024-4-29 |  | DO 제어 FC 6 적용 | IOM | 별도의 DO맵 미사용 |  | O | O
4) 2024-4-30 | V0.03 | 서버에서 Time sync address (addr 6942) | modbus | addr 6762 not used
2024-10-11 | V0.04 | IO 모듈 시간동기기능, ITIC 기능추가 | modbus
2024-12-26 | V0.05 | Modbus Rx Count 추가 | modbus | PDM에 comm LED 출력용
2025-01-09 | V0.06 | IO 모듈 설명 추가
2025-01-21 | V0.07 | 기본파 전압,전류 추가 | modbus
2025-02-05 | V0.08 | alarm, event 시 DO 출력 세팅 | modbus
2025-02-06 | V0.09 | clear alarm DO address 변경(7364->7362) | modbus
2025-02-07 | V0.091 | DO Type 추가( 2 : Event, address 7264) | modbus
2025-02-12 | V0.0A | Test Mode 추가, Do Type name 변경 | modbus
2025-02-13 | V0.0B | Alarm,Event Status 추가 | modbus
2025-02-24 | V0.0C | Test Mode, Clear PI 기능 추가 | modbus
|  | IOM Reset, Clear PI 추가 | IOM
2025-02-24 | V0.0D | RSTP status 추가 | modbus
2025-03-15 | V0.0F | ITIC Log 수정 event log page up/down command alarm log page up/down command ITIC log page up/down command | modbus

## modbus
address | name | 설명 | Unit | TYPE | FC | Word Count | Item Count
Metering | [7 empty] | 구현
0 | Time Stamp |  |  | UTC | 3 | 2 | 1
2 | Frequency | 라인주파수 | Hz | float | 3 | 2 | 1 | O
4 | Internal Temp |  | ℃ | float | 3 | 2 | 1
6 | U1 | 상전압 1 | V | float | 3 | 2 | 1 | O
8 | U2 | 상전압 2 |  | float | 3 | 2 | 1 | O
10 | U3 | 상전압 3 |  | float | 3 | 2 | 1 | O
12 | U~ | 상전압 평균 |  | float | 3 | 2 | 1 | O
14 | U12 | 선간 전압 12 |  | float | 3 | 2 | 1 | O
16 | U23 | 선간 전압 23 |  | float | 3 | 2 | 1 | O
18 | U31 | 선간 전압 31 |  | float | 3 | 2 | 1 | O
20 | Upp~ | 선간 전압 평균 |  | float | 3 | 2 | 1 | O
22 | Uunbalance2 |  | % | float | 3 | 2 | 1 | O | Uu=neg/pos*100
24 | Uunbalance0 |  |  | float | 3 | 2 | 1 | O | Uo=zero/pos*100
26 | U Zero Sequence Mag. |  |  | float | 3 | 2 | 1
28 | U Zero Sequence angle |  |  | float | 3 | 2 | 1
30 | U Positive Sequence Mag. |  |  | float | 3 | 2 | 1
32 | U Positive Sequence angle |  |  | float | 3 | 2 | 1
34 | U Negative Sequence Mag |  |  | float | 3 | 2 | 1
36 | U Negative Sequence angle |  |  | float | 3 | 2 | 1
38 | Angle U1 |  |  | float | 3 | 2 | 1
40 | Angle U2 |  |  | float | 3 | 2 | 1
42 | Angle U3 |  |  | float | 3 | 2 | 1
44 | U Underdeviation L1 |  | % | float | 3 | 2 | 1
46 | U Underdeviation L2 |  | % | float | 3 | 2 | 1
48 | U Underdeviation L3 |  | % | float | 3 | 2 | 1
50 | U Overdeviation L1 |  | % | float | 3 | 2 | 1 | O
52 | U Overdeviation L2 |  | % | float | 3 | 2 | 1 | O
54 | U Overdeviation L3 |  | % | float | 3 | 2 | 1 | O
56 |  |  |  | float | 3 | 2 | 1
58 |  |  |  | float | 3 | 2 | 1
60 | I1 | 상전류 1 | A | float | 3 | 2 | 1 | O
62 | I2 | 상전류 2 |  | float | 3 | 2 | 1 | O
64 | I3 | 상전류 3 |  | float | 3 | 2 | 1 | O
66 | I~ |  |  | float | 3 | 2 | 1 | O
68 | I total (I1+I2+I3) |  |  | float | 3 | 2 | 1 | O
70 | In(Measured) |  |  | float | 3 | 2 | 1 | O | 1. 5A: -3P4W(In) -3P3W(Ig), 2. AT/VT: Ig로 사용
72 | In(Calculated) | Ia+Ib+Ic+In = Ig |  | float | 3 | 2 | 1 | O | 1. 5A: -3P4W(Ig=Ia+Ib+Ic+In), -3P3W(Ig=Ia+Ib+Ic), 2. AT/VT: 5A와 동일
74 |  |  |  | float | 3 | 2 | 1 | O
76 | I Zero Sequence Mag |  |  | float | 3 | 2 | 1
78 | I Zero Sequence angle |  |  | float | 3 | 2 | 1
80 | I Positive Sequence Mag. |  |  | float | 3 | 2 | 1
82 | I Positive Sequence angle |  |  | float | 3 | 2 | 1
84 | I Negative Sequence Mag. |  |  | float | 3 | 2 | 1
86 | I Negative Sequence angle |  |  | float | 3 | 2 | 1
88 | Angle I1 |  |  | float | 3 | 2 | 1 | O
90 | Angle I2 |  |  | float | 3 | 2 | 1 | O
92 | Angle I3 |  |  | float | 3 | 2 | 1 | O
94 | Iunbalance2 |  | % | float | 3 | 2 | 1
96 | Iunbalance0 |  |  | float | 3 | 2 | 1
98 |  |  |  | float | 3 | 2 | 1
100 | P1 | 유효전력 P1 | W | float | 3 | 2 | 1 | O
102 | P2 | 유효전력 P2 |  | float | 3 | 2 | 1 | O
104 | P3 | 유효전력 P3 |  | float | 3 | 2 | 1 | O
106 | P total | 유효전력 P-total |  | float | 3 | 2 | 1 | O
108 | fP1 |  |  | float | 3 | 2 | 1 | O
110 | fP2 |  |  | float | 3 | 2 | 1 | O
112 | fP3 |  |  | float | 3 | 2 | 1 | O
114 | fP total |  |  | float | 3 | 2 | 1 | O
116 | Q1 | 무효전력 Q1 | VAR | float | 3 | 2 | 1 | O
118 | Q2 | 무효전력 Q2 |  | float | 3 | 2 | 1 | O
120 | Q3 | 무효전력 Q3 |  | float | 3 | 2 | 1 | O
122 | Q total | 무효전력 Q-total |  | float | 3 | 2 | 1 | O
124 | fQ1 |  |  | float | 3 | 2 | 1 | O
126 | fQ2 |  |  | float | 3 | 2 | 1 | O
128 | fQ3 |  |  | float | 3 | 2 | 1 | O
130 | fQ total |  |  | float | 3 | 2 | 1 | O
132 | S1 | 피상전력 S1 | VA | float | 3 | 2 | 1 | O
134 | S2 | 피상전력 S2 |  | float | 3 | 2 | 1 | O
136 | S3 | 피상전력 S3 |  | float | 3 | 2 | 1 | O
138 | S total | 피상전력 S-total |  | float | 3 | 2 | 1 | O
140 | fS1 |  |  | float | 3 | 2 | 1 | O
142 | fS2 |  |  | float | 3 | 2 | 1 | O
144 | fS3 |  |  | float | 3 | 2 | 1 | O
146 | fS total |  |  | float | 3 | 2 | 1 | O
148 | PF1 | 역률 PF1 | % | float | 3 | 2 | 1 | O
150 | PF2 | 역률 PF2 |  | float | 3 | 2 | 1 | O
152 | PF3 | 역률 PF3 |  | float | 3 | 2 | 1 | O
154 | PF total | 역률 PF-total |  | float | 3 | 2 | 1 | O
156 | dPF1 |  | % | float | 3 | 2 | 1
158 | dPF2 |  |  | float | 3 | 2 | 1
160 | dPF3 |  |  | float | 3 | 2 | 1
162 | dPF total |  |  | float | 3 | 2 | 1
164 | deformed Power D L1 |  | W | float | 3 | 2 | 1 |  | S=sqrt {P^{2}+Q^{2}+D^{2}}
166 | deformed Power D L2 |  |  | float | 3 | 2 | 1
168 | deformed Power D L3 |  |  | float | 3 | 2 | 1
170 | deformed Power D Total |  |  | float | 3 | 2 | 1
172 | Power Angle(atan(fPt,fQt) L1 |  | Degree | float | 3 | 2 | 1 |  | Angle between fundamental phase voltage and phase current
174 | Power Angle(atan(fPt,fQt) L2 |  |  | float | 3 | 2 | 1
176 | Power Angle(atan(fPt,fQt) L3 |  |  | float | 3 | 2 | 1
178 |  |  |  | float | 3 | 2 | 1
THD
180 | THD V1 |  | % | float | 3 | 2 | 1
182 | THD V2 |  |  | float | 3 | 2 | 1 | O | Chip에서 제공하는 결과 사용
184 | THD V3 |  |  | float | 3 | 2 | 1 | O
186 | THD V12 |  |  | float | 3 | 2 | 1 | O
188 | THD V23 |  |  | float | 3 | 2 | 1 | O
190 | THD V31 |  |  | float | 3 | 2 | 1 | O
192 | CF V1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1 | O
194 | CF V2 |  |  | float | 3 | 2 | 1
196 | CF V3 |  |  | float | 3 | 2 | 1
198 | CF V12 |  |  | float | 3 | 2 | 1
200 | CF V23 |  |  | float | 3 | 2 | 1
202 | CF V31 |  |  | float | 3 | 2 | 1
204 | THD I1 |  |  | float | 3 | 2 | 1
206 | THD I2 |  |  | float | 3 | 2 | 1
208 | THD I3 |  |  | float | 3 | 2 | 1
210 | TDD I1 |  |  | float | 3 | 2 | 1
212 | TDD I2 |  |  | float | 3 | 2 | 1
214 | TDD I3 |  |  | float | 3 | 2 | 1
216 | K I1 | K-FACTOR : 고조파 허용율 |  | float | 3 | 2 | 1
218 | K I2 |  |  | float | 3 | 2 | 1
220 | K I3 |  |  | float | 3 | 2 | 1
222 | CF I1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
224 | CF I2 |  |  | float | 3 | 2 | 1
226 | CF I3 |  |  | float | 3 | 2 | 1
228 | fU1 | 기본파 U1 |  | float | 3 | 2 | 1 | V0.07
230 | fU2 | 기본파 U2 |  | float | 3 | 2 | 1
232 | fU3 | 기본파 U3 |  | float | 3 | 2 | 1
234 | fU~ | 기본파 전압 평균 |  | float | 3 | 2 | 1
236 | fI1 | 기본파 I1 |  | float | 3 | 2 | 1
238 | fI2 | 기본파 I2 |  | float | 3 | 2 | 1
240 | fI3 | 기본파 I3 |  | float | 3 | 2 | 1
242 | fI~ | 기본파 전류 평균 |  | float | 3 | 2 | 1
244 | reserved |  |  | float | 3 | 2 | 3
IO
250 | DI[1..24] |  |  | U16 | 3 | 1 | 24
274 | DO[1..4] |  |  | U16 | 3 | 1 | 4
278 | AI[1..8] |  |  | float | 3 | 2 | 8
294 | DC[1..3] |  |  | float | 3 | 2 | 3
Energy
300 | import kwh(0 ~ 999,999,999.9 kw) | 누적 유효전력량 |  | U32 | 3 | 2 | 1 | 300
302 | export kwh |  |  | U32 | 3 | 2 | 1
304 | import kvarh |  |  | U32 | 3 | 2 | 1
306 | export kvarh |  |  | U32 | 3 | 2 | 1
308 | kvah |  |  | U32 | 3 | 2 | 1
310 |  |  |  | U32 | 3 | 2 | 1
312 | import kwh this month |  |  | U32 | 3 | 2 | 1
314 | export kwh this month |  |  | U32 | 3 | 2 | 1
316 | import kvarh this month |  |  | U32 | 3 | 2 | 1
318 | export kvarh this month |  |  | U32 | 3 | 2 | 1
320 | kvah this month |  |  | U32 | 3 | 2 | 1
322 |  |  |  | U32 | 3 | 2 | 1
324 | import kwh last month |  |  | U32 | 3 | 2 | 1
326 | export kwh last month |  |  | U32 | 3 | 2 | 1
328 | import kvarh last month |  |  | U32 | 3 | 2 | 1
330 | export kvarh last month |  |  | U32 | 3 | 2 | 1
332 | kvah last month |  |  | U32 | 3 | 2 | 1
334 |  |  |  | U32 | 3 | 2 | 1
336 | import wh | 0~99,999,999.999 w |  | U64 | 3 | 4 | 1
340 | export wh |  |  | U64 | 3 | 4 | 1
344 | import varh |  |  | U64 | 3 | 4 | 1
348 | export varh |  |  | U64 | 3 | 4 | 1
352 | vah |  |  | U64 | 3 | 4 | 1
356 |  |  |  | U64 | 3 | 4 | 1
360 |  |  |  | U32 |  | 2 | 20
Demand
400 | Time Stamp |  |  | UTC | 3 | 2 | 1 | 400
402 | Max Demand P(import) |  |  | float | 3 | 2 | 1
404 | Time Stamp |  |  | UTC | 3 | 2 | 1
406 | Max Demand P(export) |  |  | float | 3 | 2 | 1
408 | Time Stamp |  |  | UTC | 3 | 2 | 1
410 | Max Demand Q(import) |  |  | float | 3 | 2 | 1
412 | Time Stamp |  |  | UTC | 3 | 2 | 1
414 | Max Demand Q(export) |  |  | float | 3 | 2 | 1
416 | Time Stamp |  |  | UTC | 3 | 2 | 1
418 | Max Demand S |  |  | float | 3 | 2 | 1
420 | Time Stamp |  |  | UTC | 3 | 2 | 1
422 | Max Demand I1 |  |  | float | 3 | 2 | 1
424 | Time Stamp |  |  | UTC | 3 | 2 | 1
426 | Max Demand I2 |  |  | float | 3 | 2 | 1
428 | Time Stamp |  |  | UTC | 3 | 2 | 1
430 | Max Demand I3 |  |  | float | 3 | 2 | 1
432 | Demand time stamp |  |  | UTC | 3 | 2 | 1
434 | Demand P(import) |  |  | float | 3 | 2 | 1
436 | Demand P(export) |  |  | float | 3 | 2 | 1 | 812 | 최근 24시간 그래프 그린다
438 | Demand Q(import) |  |  | float | 3 | 2 | 1
440 | Demand Q(export) |  |  | float | 3 | 2 | 1
442 | Demand S(export) |  |  | float | 3 | 2 | 1
444 | Demand I1 |  |  | float | 3 | 2 | 1
446 | Demand I2 |  |  | float | 3 | 2 | 1
448 | Demand I3 |  |  | float | 3 | 2 | 1
450 | Present Demand P(import) |  |  | float | 3 | 2 | 1
452 | Present Demand P(export) |  |  | float | 3 | 2 | 1
454 | Present Demand Q(import) |  |  | float | 3 | 2 | 1
456 | Present Demand Q(export) |  |  | float | 3 | 2 | 1
458 | Present Demand S(export) |  |  | float | 3 | 2 | 1
460 | Forecast Demand P(export) |  |  | float | 3 | 2 | 1
462 | Demand P 15m(import) |  |  | float | 3 | 2 | 1
464 |  |  |  | float | 3 | 2 | 1
466 |  |  |  | float | 3 | 2 | 1
468 | Time Stamp(Demand Log 시작일) |  |  | U32 | 3 | 2 | 1
470 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
662 |  |  |  | float | 3 | 2 | 19
Voltage Quality RealTime Value
700 | Voltage Under Deviation L1 |  |  | float | 3 | 2 | 1
702 | Voltage Under Deviation L2 |  |  | float | 3 | 2 | 1
704 | Voltage Under Deviation L3 |  |  | float | 3 | 2 | 1
706 | Voltage Over Deviation L1 |  |  | float | 3 | 2 | 1
708 | Voltage Over Deviation L2 |  |  | float | 3 | 2 | 1
710 | Voltage Over Deviation L3 |  |  | float | 3 | 2 | 1
712 | Flickers Pi L1 |  |  | float | 3 | 2 | 1
714 | Flickers Pi L2 |  |  | float | 3 | 2 | 1
716 | Flickers Pi L3 |  |  | float | 3 | 2 | 1
718 | Flicker Pim L1 |  |  | float | 3 | 2 | 1
720 | Flicker Pim L2 |  |  | float | 3 | 2 | 1
722 | Flicker Pim L3 |  |  | float | 3 | 2 | 1
724 | Flicker Pst L1 |  |  | float | 3 | 2 | 1
726 | Flicker Pst L2 |  |  | float | 3 | 2 | 1
728 | Flicker Pst L3 |  |  | float | 3 | 2 | 1
730 | Flicker Plt L1 |  |  | float | 3 | 2 | 1
732 | Flicker Plt L2 |  |  | float | 3 | 2 | 1
734 | Flicker Plt L3 |  |  | float | 3 | 2 | 1
736 | Signaling Volt L1 |  |  | float | 3 | 2 | 1
738 | Signaling Volt L2 |  |  | float | 3 | 2 | 1
740 | Signaling Volt L3 |  |  | float | 3 | 2 | 1
742 |  |  |  | float |  | 2 | 29
EN50160 Last Week
800 | start date |  |  | UTC | 3 | 2 | 1
802 | end date |  |  | UTC | 3 | 2 | 1
804 | status&compliance | bit 0: Freq Var1 bit 1: Freq Var2 bit 2: Volt Var1 L1 bit 3: Volt Var1 L2 bit 4: Volt Var1 L3 bit 5: Volt Var2 L1 bit 6: Volt Var2 L2 bit 7: Volt Var2 L3 bit 8: Unbalance bit 9: Volt THD L1 bit 10: Volt THD L2 bit 11: Volt THD L3 bit 12: Volt HD L1 bit 13: Volt HD L2 bit 14: Volt HD L3 bit 15: Pst L1 bit 16: Pst L2 bit 17: Pst L3 bit 18: Plt L1 bit 19: Plt L2 bit 20: Plt L3 bit 21: SigVolt L1 bit 22: SigVolt L2 bit 23: SigVolt L3 bit 31: Complete [status] 0: OK 1: failed |  | U32 | 3 | 2 | 1
806 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1 |  | 95%/Week
807 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1 |  | Info Only
808 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
809 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
810 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1 |  | 95%/Week
811 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
812 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
813 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1 |  | Info Only
814 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
815 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
816 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1 |  | Info Only
817 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
818 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
819 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1 |  | Info Only
820 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
821 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
822 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1 |  | Info Only
823 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
824 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
825 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1 |  | 95%/Week
826 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
827 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
828 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1 |  | 95%/Week
829 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
830 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
831 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1 |  | 99%/Day
832 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
833 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
834 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
835 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
836 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
837 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
838 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
839 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
840 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
841 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
842 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
843 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
844 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
845 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
846 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
847 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
848 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
849 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
EN50160 Last Week
850 | start date |  |  | UTC | 3 | 2 | 1 | 850
852 | end date |  |  | UTC | 3 | 2 | 1
854 | status |  |  | U16 | 3 | 1 | 1
855 | compilance |  |  | U16 | 3 | 1 | 1
856 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1
857 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1
858 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
859 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
860 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1
861 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
862 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
863 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1
864 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
865 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
866 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1
867 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
868 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
869 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1
870 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
871 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
872 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1
873 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
874 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
875 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1
876 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
877 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
878 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1
879 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
880 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
881 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1 | 캐리어 신호의 크기
882 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
883 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
884 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
885 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
886 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
887 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
888 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
889 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
890 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
891 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
892 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
893 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
894 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
895 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
896 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
897 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
898 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
899 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
Harmonics
900 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
964 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
1028 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
1092 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
1156 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
1220 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
1284 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
1348 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
1412 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
1476 |  |  |  | S16 |  | 1 | 24 | 576
Inter Harmonics
1500 | Harmonics V1 |  |  | S16 | 3 | 1 | 80
1580 | Harmonics V2 |  |  | S16 | 3 | 1 | 80
1660 | Harmonics V3 |  |  | S16 | 3 | 1 | 80
1740 | Harmonics V12 |  |  | S16 | 3 | 1 | 80
1820 | Harmonics V23 |  |  | S16 | 3 | 1 | 80
1900 | Harmonics V31 |  |  | S16 | 3 | 1 | 80
1980 | Harmonics I1 |  |  | S16 | 3 | 1 | 80
2060 | Harmonics I2 |  |  | S16 | 3 | 1 | 80
2140 | Harmonics I3 |  |  | S16 | 3 | 1 | 80
2220 | reserved |  |  | S16 |  | 1 | 80
Wave Sample | [8 empty] | 32K: 67,107,786 8K: 74,518,668 첫번째 번지 접근시 wave data를 modbus map으로 load 한다
2300 | Wave Form V1 (160 sample) |  |  | S16 | 3 | 1 | 160
2460 | Wave Form V2 (160 sample) |  |  | S16 | 3 | 1 | 160
2620 | Wave Form V3 (160 sample) |  |  | S16 | 3 | 1 | 160
2780 | Wave Form V12 (160 sample) |  |  | S16 | 3 | 1 | 160
2940 | Wave Form V23 (160 sample) |  |  | S16 | 3 | 1 | 160
3100 | Wave Form V31 (160 sample) |  |  | S16 | 3 | 1 | 160
3260 | Wave Form I1 (160 sample) |  |  | S16 | 3 | 1 | 160
3420 | Wave Form I2 (160 sample) |  |  | S16 | 3 | 1 | 160
3580 | Wave Form I3 (160 sample) |  |  | S16 | 3 | 1 | 160
3740 | vscale |  |  | float | 3 | 2 | 1
3742 | iscale |  |  | float | 3 | 2 | 1
3744 | reserved |  |  | S16 |  | 1 | 56
Max/Min
3800 | fr |  |  | S16 | 3 | 1 | 1 | 3800
3801 | re |  |  | S16 | 3 | 1 | 1
3802 | Reset TimeStamp |  |  | UTC | 3 | 2 | 1
3804 | Frequency | Max |  | float | 3 | 2 | 1
3806 |  | Max TimeStamp |  | U32 | 3 | 2 | 1
3808 |  | Min |  | float | 3 | 2 | 1
3810 |  | Min TimeStamp |  | U32 | 3 | 2 | 1
3812 | Temp |  |  | float | 3 | 2 | 4
3820 | U1 |  |  | float | 3 | 2 | 4
3828 | U2 |  |  | float | 3 | 2 | 4
3836 | U3 |  |  | float | 3 | 2 | 4
3844 | U~ |  |  | float | 3 | 2 | 4
3852 | U12 |  |  | float | 3 | 2 | 4
3860 | U23 |  |  | float | 3 | 2 | 4
3868 | U31 |  |  | float | 3 | 2 | 4
3876 | Upp~ |  |  | float | 3 | 2 | 4
3884 | I1 |  |  | float | 3 | 2 | 4
3892 | I2 |  |  | float | 3 | 2 | 4
3900 | I3 |  |  | float | 3 | 2 | 4
3908 | I~ |  |  | float | 3 | 2 | 4
3916 | I total |  |  | float | 3 | 2 | 4
3924 | In |  |  | float | 3 | 2 | 4
3932 | Isum |  |  | float | 3 | 2 | 4
3940 | P1 |  |  | float | 3 | 2 | 4
3948 | P2 |  |  | float | 3 | 2 | 4
3956 | P3 |  |  | float | 3 | 2 | 4
3964 | P total |  |  | float | 3 | 2 | 4
3972 | Q1 |  |  | float | 3 | 2 | 4
3980 | Q2 |  |  | float | 3 | 2 | 4
3988 | Q3 |  |  | float | 3 | 2 | 4
3996 | Q total |  |  | float | 3 | 2 | 4
4004 | S1 |  |  | float | 3 | 2 | 4
4012 | S2 |  |  | float | 3 | 2 | 4
4020 | S3 |  |  | float | 3 | 2 | 4
4028 | S total |  |  | float | 3 | 2 | 4
4036 | PF L1 |  |  | float | 3 | 2 | 4
4044 | PF L2 |  |  | float | 3 | 2 | 4
4052 | PF L3 |  |  | float | 3 | 2 | 4
4060 | PF total |  |  | float | 3 | 2 | 4
4068 | THD U1 |  |  | float | 3 | 2 | 4
4076 | THD U2 |  |  | float | 3 | 2 | 4
4084 | THD U3 |  |  | float | 3 | 2 | 4
4092 | THD U12 |  |  | float | 3 | 2 | 4
4100 | THD U23 |  |  | float | 3 | 2 | 4
4108 | THD U31 |  |  | float | 3 | 2 | 4
4116 | THD I1 |  |  | float | 3 | 2 | 4
4124 | THD I2 |  |  | float | 3 | 2 | 4
4132 | THD I3 |  |  | float | 3 | 2 | 4
4140 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
4142 | reserved |  |  | U16 | 3 | 1 | 1
4143 | CRC |  |  | U16 | 3 | 1 | 1
4144 |  |  |  | U16 |  | 1 | 56
alarm status
4200 | fr |  |  | U16 | 3 | 1 | 1
4201 | re |  |  | U16 | 3 | 1 | 1
4202 | reset Ts |  |  | UTC | 3 | 2 | 1
4204 | Alarm State #1 | Alarm Channel |  | U16 | 3 | 1 | 1
4205 |  | Alarm Condition |  | U16 | 3 | 1 | 1
4206 |  | Alarm Level |  | float | 3 | 2 | 1
4208 |  | Alarm Status |  | U16 | 3 | 1 | 1
4209 |  | Alarm Count |  | U16 | 3 | 1 | 1
4210 | Alarm State #2 |  |  | U16 | 3 | 1 | 6
4216 | Alarm State #3 |  |  | U16 | 3 | 1 | 6
4222 | Alarm State #4 |  |  | U16 | 3 | 1 | 6
4228 | Alarm State #5 |  |  | U16 | 3 | 1 | 6
4234 | Alarm State #6 |  |  | U16 | 3 | 1 | 6
4240 | Alarm State #7 |  |  | U16 | 3 | 1 | 6
4246 | Alarm State #8 |  |  | U16 | 3 | 1 | 6
4252 | Alarm State #9 |  |  | U16 | 3 | 1 | 6
4258 | Alarm State #10 |  |  | U16 | 3 | 1 | 6
4264 | Alarm State #11 |  |  | U16 | 3 | 1 | 6
4270 | Alarm State #12 |  |  | U16 | 3 | 1 | 6
4276 | Alarm State #13 |  |  | U16 | 3 | 1 | 6
4282 | Alarm State #14 |  |  | U16 | 3 | 1 | 6
4288 | Alarm State #15 |  |  | U16 | 3 | 1 | 6
4294 | Alarm State #16 |  |  | U16 | 3 | 1 | 6
4300 | Alarm State #17 |  |  | U16 | 3 | 1 | 6
4306 | Alarm State #18 |  |  | U16 | 3 | 1 | 6
4312 | Alarm State #19 |  |  | U16 | 3 | 1 | 6
4318 | Alarm State #20 |  |  | U16 | 3 | 1 | 6
4324 | Alarm State #21 |  |  | U16 | 3 | 1 | 6
4330 | Alarm State #22 |  |  | U16 | 3 | 1 | 6
4336 | Alarm State #23 |  |  | U16 | 3 | 1 | 6
4342 | Alarm State #24 |  |  | U16 | 3 | 1 | 6
4348 | Alarm State #25 |  |  | U16 | 3 | 1 | 6
4354 | Alarm State #26 |  |  | U16 | 3 | 1 | 6
4360 | Alarm State #27 |  |  | U16 | 3 | 1 | 6
4366 | Alarm State #28 |  |  | U16 | 3 | 1 | 6
4372 | Alarm State #29 |  |  | U16 | 3 | 1 | 6
4378 | Alarm State #30 |  |  | U16 | 3 | 1 | 6
4384 | Alarm State #31 |  |  | U16 | 3 | 1 | 6
4390 | Alarm State #32 |  |  | U16 | 3 | 1 | 6
4396 | update Ts |  |  | U32 | 3 | 2 | 1
4398 | Global Alarm Status(alarm 하나라도 있으면 1, 아니면 0) |  |  | U16 | 3 | 1 | 1
4399 |  |  |  | U16 |  | 1 | 1
alarm log
4400 | total count | 0 ~ 1023 |  | U16 | 3 | 1 | 1
4401 | start | 0 ~ 1023 |  | U16 | 3 | 1 | 1
4402 | end | 0 ~ 1023 |  | U16 | 3 | 1 | 1
4403 | seq | 이벤트 발생시 증가 |  | U16 | 3 | 1 | 1
4404 | Alarm Log #1 | Time Stamp |  | UTC | 3 | 2 | 1 |  | 2019-5-11변경
4406 |  | status |  | U16 | 3 | 1 | 1
4407 |  | Alarm Channel & Condition |  | U16 | 3 | 1 | 1
4408 |  | level |  | float | 3 | 2 | 1
4410 |  | Value |  | float | 3 | 2 | 1
4412 | Alarm Log #2 |  |  | U16 | 3 | 1 | 8
4420 | Alarm Log #3 |  |  | U16 | 3 | 1 | 8
4428 | Alarm Log #4 |  |  | U16 | 3 | 1 | 8
4436 | Alarm Log #5 |  |  | U16 | 3 | 1 | 8
4444 | Alarm Log #6 |  |  | U16 | 3 | 1 | 8
4452 | Alarm Log #7 |  |  | U16 | 3 | 1 | 8
4460 | Alarm Log #8 |  |  | U16 | 3 | 1 | 8
4468 | Alarm Log #9 |  |  | U16 | 3 | 1 | 8
4476 | Alarm Log #10 |  |  | U16 | 3 | 1 | 8
4484 | Alarm Log #11 |  |  | U16 | 3 | 1 | 8
4492 | Alarm Log #12 |  |  | U16 | 3 | 1 | 8
4500 | Alarm Log #13 |  |  | U16 | 3 | 1 | 8
4508 | Alarm Log #14 |  |  | U16 | 3 | 1 | 8
4516 | Alarm Log #15 |  |  | U16 | 3 | 1 | 8
4524 | Alarm Log #16 |  |  | U16 | 3 | 1 | 8
4532 | Alarm Log #17 |  |  | U16 | 3 | 1 | 8
4540 | Alarm Log #18 |  |  | U16 | 3 | 1 | 8
4548 | Alarm Log #19 |  |  | U16 | 3 | 1 | 8
4556 | Alarm Log #20 |  |  | U16 | 3 | 1 | 8
4564 | Alarm Log #21 |  |  | U16 | 3 | 1 | 8
4572 | Alarm Log #22 |  |  | U16 | 3 | 1 | 8
4580 | Alarm Log #23 |  |  | U16 | 3 | 1 | 8
4588 | Alarm Log #24 |  |  | U16 | 3 | 1 | 8
4596 | Alarm Log #25 |  |  | U16 | 3 | 1 | 8
4604 | Alarm Log #26 |  |  | U16 | 3 | 1 | 8
4612 | Alarm Log #27 |  |  | U16 | 3 | 1 | 8
4620 | Alarm Log #28 |  |  | U16 | 3 | 1 | 8
4628 | Alarm Log #29 |  |  | U16 | 3 | 1 | 8
4636 | Alarm Log #30 |  |  | U16 | 3 | 1 | 8
4644 | Alarm Log #31 |  |  | U16 | 3 | 1 | 8
4652 | Alarm Log #32 |  |  | U16 | 3 | 1 | 8
4660 |  |  |  | U16 |  | 1 | 40
이벤트 리스트
4700 | total count | 0 ~ 1023 |  | U16 | 3 | 1 | 1 | 4500
4701 | start | 0 ~ 1023 |  | U16 | 3 | 1 | 1
4702 | end | 0 ~ 1023 |  | U16 | 3 | 1 | 1
4703 | seq | 이벤트 발생시 증가 |  | U16 | 3 | 1 | 1
PQ 이벤트(Sag, Swell, Transient, OC)
4704 | start ts |  |  | UTC | 3 | 2 | 1
4706 | start ts(ms) |  |  | U16 | 3 | 1 | 1
4707 | duration |  |  | U16 | 3 | 1 | 1
4708 | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only |  | U16 | 3 | 1 | 1
4709 | mask |  |  | U16 | 3 | 1 | 1
4710 | Level 1 |  |  | float | 3 | 2 | 1
4712 | Level 2 |  |  | float | 3 | 2 | 1
4714 | Level 3 |  |  | float | 3 | 2 | 1
4716 | PQ Event #2 |  |  | U16 | 3 | 1 | 12
4728 | PQ Event #3 |  |  | U16 | 3 | 1 | 12
4740 | PQ Event #4 |  |  | U16 | 3 | 1 | 12
4752 | PQ Event #5 |  |  | U16 | 3 | 1 | 12
4764 | PQ Event #6 |  |  | U16 | 3 | 1 | 12
4776 | PQ Event #7 |  |  | U16 | 3 | 1 | 12
4788 | PQ Event #8 |  |  | U16 | 3 | 1 | 12
4800 | PQ Event #9 |  |  | U16 | 3 | 1 | 12
4812 | PQ Event #10 |  |  | U16 | 3 | 1 | 12
4824 | PQ Event #11 |  |  | U16 | 3 | 1 | 12
4836 | PQ Event #12 |  |  | U16 | 3 | 1 | 12
4848 | PQ Event #13 |  |  | U16 | 3 | 1 | 12
4860 | PQ Event #14 |  |  | U16 | 3 | 1 | 12
4872 | PQ Event #15 |  |  | U16 | 3 | 1 | 12
4884 | PQ Event #16 |  |  | U16 | 3 | 1 | 12
4896 | PQ Event #17 |  |  | U16 | 3 | 1 | 12
4908 | PQ Event #18 |  |  | U16 | 3 | 1 | 12
4920 | PQ Event #19 |  |  | U16 | 3 | 1 | 12
4932 | PQ Event #20 |  |  | U16 | 3 | 1 | 12
4944 | PQ Event #21 |  |  | U16 | 3 | 1 | 12
4956 | PQ Event #22 |  |  | U16 | 3 | 1 | 12
4968 | PQ Event #23 |  |  | U16 | 3 | 1 | 12
4980 | PQ Event #24 |  |  | U16 | 3 | 1 | 12
4992 | PQ Event #25 |  |  | U16 | 3 | 1 | 12
5004 | PQ Event #26 |  |  | U16 | 3 | 1 | 12
5016 | PQ Event #27 |  |  | U16 | 3 | 1 | 12
5028 | PQ Event #28 |  |  | U16 | 3 | 1 | 12
5040 | PQ Event #29 |  |  | U16 | 3 | 1 | 12
5052 | PQ Event #30 |  |  | U16 | 3 | 1 | 12
5064 | PQ Event #31 |  |  | U16 | 3 | 1 | 12
5076 | PQ Event #32 |  |  | U16 | 3 | 1 | 12
5088 |  |  |  | U16 | 3 | 1 | 2
PQ Event Counter
5090 | Transient Voltage Count |  |  | U16 | 3 | 1 | 1
5091 | Transient Current Count |  |  | U16 | 3 | 1 | 1
5092 | OC Count |  |  | U16 | 3 | 1 | 1
5093 | Sag Coount |  |  | U16 | 3 | 1 | 1
5094 | Swell Count |  |  | U16 | 3 | 1 | 1
5095 | Interrupt Count |  |  | U16 | 3 | 1 | 1
5096 |  |  |  | U16 | 3 | 1 | 1
5097 |  |  |  | U16 | 3 | 1 | 1
5098 |  |  |  | U16 | 3 | 1 | 1
5099 |  |  |  | U16 | 3 | 1 | 1
월간리포트 생성위한 10분 평균
5100 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
5102 | U1 |  |  | float | 3 | 2 | 1
5104 | U2 |  |  | float | 3 | 2 | 1
5106 | U3 |  |  | float | 3 | 2 | 1
5108 | U THD1 |  |  | float | 3 | 2 | 1
5110 | U THD2 |  |  | float | 3 | 2 | 1
5112 | U THD3 |  |  | float | 3 | 2 | 1
5114 | Upp THD1 |  |  | float | 3 | 2 | 1
5116 | Upp THD2 |  |  | float | 3 | 2 | 1
5118 | Upp THD3 |  |  | float | 3 | 2 | 1
5120 | U Unbal Uu |  |  | float | 3 | 2 | 1
5122 | U Unbal Uo |  |  | float | 3 | 2 | 1
5124 | I1 |  |  | float | 3 | 2 | 1
5126 | I2 |  |  | float | 3 | 2 | 1
5128 | I3 |  |  | float | 3 | 2 | 1
5130 | In |  |  | float | 3 | 2 | 1
5132 | I THD1 |  |  | float | 3 | 2 | 1
5134 | I THD2 |  |  | float | 3 | 2 | 1
5136 | I THD3 |  |  | float | 3 | 2 | 1
5138 | I TDD1 |  |  | float | 3 | 2 | 1
5140 | I TDD2 |  |  | float | 3 | 2 | 1
5142 | I TDD3 |  |  | float | 3 | 2 | 1
5144 | K-factor 1 |  |  | float | 3 | 2 | 1
5146 | K-factor 2 |  |  | float | 3 | 2 | 1
5148 | K-factor 3 |  |  | float | 3 | 2 | 1
5150 | I Unbal Iu |  |  | float | 3 | 2 | 1
5152 | I Unbal Io |  |  | float | 3 | 2 | 1
5154 | kw imp |  |  | float | 3 | 2 | 1
5156 | kw exp |  |  | float | 3 | 2 | 1
5158 | kvar lag |  |  | float | 3 | 2 | 1
5160 | kvar lead |  |  | float | 3 | 2 | 1
5162 | kVA |  |  | float | 3 | 2 | 1
5164 | PF |  |  | float | 3 | 2 | 1
5166 | dPF |  |  | float | 3 | 2 | 1
5168 | temperature #1 |  |  | float | 3 | 2 | 1
5170 | temperature #2 | 온도센서 |  | float | 3 | 2 | 1
5172 | temperature #3 |  |  | float | 3 | 2 | 1
5174 | temperature #4 |  |  | float | 3 | 2 | 1
5176 | temperature #5 |  |  | float | 3 | 2 | 1
5178 | Harmonics V1 | 2nd~25th |  | S16 | 3 | 1 | 24
5202 | Harmonics V2 |  |  | S16 | 3 | 1 | 24
5226 | Harmonics V3 |  |  | S16 | 3 | 1 | 24
5250 | Harmonics V12 |  |  | S16 | 3 | 1 | 24 |  | *통신이 끊어진 경우 복구를 위해 사용된다
5274 | Harmonics V23 |  |  | S16 | 3 | 1 | 24
5298 | Harmonics V31 |  |  | S16 | 3 | 1 | 24 |  | demand
5322 | Harmonics I1 |  |  | S16 | 3 | 1 | 24
5346 | Harmonics I2 |  |  | S16 | 3 | 1 | 24
5370 | Harmonics I3 |  |  | S16 | 3 | 1 | 24
5394 |  |  |  | U16 |  | 1 | 6
Energy log
5400 | Time Stamp |  |  | UTC | 3 | 2 | 1
5402 | kwh import |  |  | float | 3 | 2 | 1
5404 | kvarh lag |  |  | float | 3 | 2 | 1
5406 | kvarh lead |  |  | float | 3 | 2 | 1
5408 | kVAh |  |  | float | 3 | 2 | 1
5410 | energy log last day 01h |  |  | float | 3 | 2 | 4
5418 | energy log last day 02h |  |  | float | 3 | 2 | 4
5426 | energy log last day 03h |  |  | float | 3 | 2 | 4
5434 | energy log last day 04h |  |  | float | 3 | 2 | 4
5442 | energy log last day 05h |  |  | float | 3 | 2 | 4
5450 | energy log last day 06h |  |  | float | 3 | 2 | 4
5458 | energy log last day 07h |  |  | float | 3 | 2 | 4
5466 | energy log last day 08h |  |  | float | 3 | 2 | 4
5474 | energy log last day 09h |  |  | float | 3 | 2 | 4
5482 | energy log last day 10h |  |  | float | 3 | 2 | 4
5490 | energy log last day 11h |  |  | float | 3 | 2 | 4
5498 | energy log last day 12h |  |  | float | 3 | 2 | 4
5506 | energy log last day 13h |  |  | float | 3 | 2 | 4
5514 | energy log last day 14h |  |  | float | 3 | 2 | 4
5522 | energy log last day 15h |  |  | float | 3 | 2 | 4
5530 | energy log last day 16h |  |  | float | 3 | 2 | 4
5538 | energy log last day 17h |  |  | float | 3 | 2 | 4
5546 | energy log last day 18h |  |  | float | 3 | 2 | 4
5554 | energy log last day 19h |  |  | float | 3 | 2 | 4
5562 | energy log last day 20h |  |  | float | 3 | 2 | 4
5570 | energy log last day 21h |  |  | float | 3 | 2 | 4
5578 | energy log last day 22h |  |  | float | 3 | 2 | 4
5586 | energy log last day 23h |  |  | float | 3 | 2 | 4
5594 |  |  |  | U16 | 3 | 1 | 6
5600 | Time Stamp |  |  | UTC | 3 | 2 | 1
5602 | kwh import |  |  | float | 3 | 2 | 1
5604 | kvarh lag |  |  | float | 3 | 2 | 1
5606 | kvarh lead |  |  | float | 3 | 2 | 1
5608 | kVAh |  |  | float | 3 | 2 | 1
5610 | energy log this day 01h |  |  | float | 3 | 2 | 4
5618 | energy log this day 02h |  |  | float | 3 | 2 | 4
5626 | energy log this day 03h |  |  | float | 3 | 2 | 4
5634 | energy log this day 04h |  |  | float | 3 | 2 | 4
5642 | energy log this day 05h |  |  | float | 3 | 2 | 4
5650 | energy log this day 06h |  |  | float | 3 | 2 | 4
5658 | energy log this day 07h |  |  | float | 3 | 2 | 4
5666 | energy log this day 08h |  |  | float | 3 | 2 | 4
5674 | energy log this day 09h |  |  | float | 3 | 2 | 4
5682 | energy log this day 10h |  |  | float | 3 | 2 | 4
5690 | energy log this day 11h |  |  | float | 3 | 2 | 4
5698 | energy log this day 12h |  |  | float | 3 | 2 | 4
5706 | energy log this day 13h |  |  | float | 3 | 2 | 4
5714 | energy log this day 14h |  |  | float | 3 | 2 | 4
5722 | energy log this day 15h |  |  | float | 3 | 2 | 4
5730 | energy log this day 16h |  |  | float | 3 | 2 | 4
5738 | energy log this day 17h |  |  | float | 3 | 2 | 4
5746 | energy log this day 18h |  |  | float | 3 | 2 | 4 |  | 전일 디멘트 로그
5754 | energy log this day 19h |  |  | float | 3 | 2 | 4
5762 | energy log this day 20h |  |  | float | 3 | 2 | 4
5770 | energy log this day 21h |  |  | float | 3 | 2 | 4
5778 | energy log this day 22h |  |  | float | 3 | 2 | 4
5786 | energy log this day 23h |  |  | float | 3 | 2 | 4
5794 |  |  |  | U16 | 3 | 1 | 6
demand log last day
5800 | Time Stamp |  |  | U32 | 3 | 2 | 1
5802 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
5994 |  |  |  | U16 | 3 | 1 | 6
Max/Min last data
6000 | fr |  |  | S16 | 3 | 1 | 1
6001 | re |  |  | S16 | 3 | 1 | 1
6002 | Reset TimeStamp |  |  | UTC | 3 | 2 | 1
6004 | Frequency |  |  | float | 3 | 2 | 4
6012 | Temp |  |  | float | 3 | 2 | 4
6020 | U1 |  |  | float | 3 | 2 | 4
6028 | U2 |  |  | float | 3 | 2 | 4
6036 | U3 |  |  | float | 3 | 2 | 4
6044 | U~ |  |  | float | 3 | 2 | 4
6052 | U12 |  |  | float | 3 | 2 | 4
6060 | U23 |  |  | float | 3 | 2 | 4
6068 | U31 |  |  | float | 3 | 2 | 4
6076 | Upp~ |  |  | float | 3 | 2 | 4
6084 | I1 |  |  | float | 3 | 2 | 4
6092 | I2 |  |  | float | 3 | 2 | 4
6100 | I3 |  |  | float | 3 | 2 | 4
6108 | I~ |  |  | float | 3 | 2 | 4
6116 | I total |  |  | float | 3 | 2 | 4
6124 | In |  |  | float | 3 | 2 | 4
6132 | Isum |  |  | float | 3 | 2 | 4
6140 | P1 |  |  | float | 3 | 2 | 4
6148 | P2 |  |  | float | 3 | 2 | 4
6156 | P3 |  |  | float | 3 | 2 | 4
6164 | P total |  |  | float | 3 | 2 | 4
6172 | Q1 |  |  | float | 3 | 2 | 4
6180 | Q2 |  |  | float | 3 | 2 | 4
6188 | Q3 |  |  | float | 3 | 2 | 4
6196 | Q total |  |  | float | 3 | 2 | 4
6204 | S1 |  |  | float | 3 | 2 | 4
6212 | S2 |  |  | float | 3 | 2 | 4
6220 | S3 |  |  | float | 3 | 2 | 4
6228 | S total |  |  | float | 3 | 2 | 4
6236 | PF L1 |  |  | float | 3 | 2 | 4
6244 | PF L2 |  |  | float | 3 | 2 | 4
6252 | PF L3 |  |  | float | 3 | 2 | 4
6260 | PF total |  |  | float | 3 | 2 | 4
6268 | THD U1 |  |  | float | 3 | 2 | 4
6276 | THD U2 |  |  | float | 3 | 2 | 4
6284 | THD U3 |  |  | float | 3 | 2 | 4
6292 | THD U12 |  |  | float | 3 | 2 | 4
6300 | THD U23 |  |  | float | 3 | 2 | 4
6308 | THD U31 |  |  | float | 3 | 2 | 4
6316 | THD I1 |  |  | float | 3 | 2 | 4
6324 | THD I2 |  |  | float | 3 | 2 | 4
6332 | THD I3 |  |  | float | 3 | 2 | 4
6340 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
6342 | reserved |  |  | U16 | 3 | 1 | 1
6343 | CRC |  |  | U16 | 3 | 1 | 1
6344 |  |  |  | U16 |  | 1 | 56
6400 |  |  |  | U16 | 3 | 1 | 2
6402 |  |  |  | U16 |  | 1 | 98
6500 |  |  |  | U16 | 3 | 1 | 1
6501 |  |  |  | U16 | 3 | 1 | 1
6502 |  |  |  | U16 |  | 1 | 1
6503 |  |  |  | U16 |  | 1 | 1
6504 |  |  |  | U16 | 3 | 1 | 1
6505 |  |  |  | U16 |  | 1 | 1
6506 |  |  |  | U16 |  | 1 | 1
6507 |  |  |  | U16 |  | 1 | 1
6508 |  |  |  | U16 | 3 | 1 | 1
6509 |  |  |  | U16 |  | 1 | 1
6510 |  |  |  | U16 |  | 1 | 1
6511 |  |  |  | U16 |  | 1 | 1
6512 |  |  |  | U16 |  | 1 | 1
6513 |  |  |  | U16 |  | 1 | 1
6514 |  |  |  | U16 |  | 1 | 1
6515 |  |  |  | U16 |  | 1 | 1
6516 |  |  |  | U16 |  | 1 | 4
IOM Data
6520 | hbeat |  |  | U16 | 3 | 1 | 1
6521 | type | 1 : DI24,DO6,AI6 |  | U16 | 3 | 1 | 1
6522 | dbflag |  |  | U16 | 3 | 1 | 1
6523 | subtype |  |  | U16 | 3 | 1 | 1
6524 | DI 0~31 |  |  | U16 | 3 | 1 | 32
6556 | DO 0~7 |  |  | U16 | 3,6 | 1 | 8
6564 | AI 0~7 |  |  | float | 3 | 2 | 8
6580 | DC V |  |  | float | 3 | 2 | 1
6582 | DC I1 |  |  | float | 3 | 2 | 1
6584 | DC I2 |  |  | float | 3 | 2 | 1
6586 | reserved |  |  | U16 |  | 1 | 54
METER INFO
6640 | serial# |  |  | U16 | 3 | 1 | 6
6646 | mac address |  |  | U16 | 3 | 1 | 4
6650 | HW Model |  |  | U16 | 3 | 1 | 1
6651 | HW version |  |  | U16 | 3 | 1 | 1
6652 | FW version |  |  | U16 | 3 | 1 | 1
6653 | FW_BUILD_YEAR |  |  | U16 | 3 | 1 | 1
6654 | FW_BUILD_MON |  |  | U16 | 3 | 1 | 1
6655 | FW_BUILD_DAY |  |  | U16 | 3 | 1 | 1
6656 | Modbus Rx Count | PDM Comm LED toggle 사용 |  | U16 | 3 | 1 | 1
6657 | Alarm Status | Alarm Ack 시 0으로 초기화, Alarm 발생시 1 |  | U16 | 3 | 1 | 1
6658 | Event Status |  |  | U16 | 3 | 1 | 1
6659 | LAN HUB#1 RSTP Status | 0 : disable, 1 : broken, 2 : blocking, 3 : listening, 4 : learning, 5 : forwarding |  | U16 | 3 | 1 | 1
6660 | LAN HUB#2 RSTP Status |  |  | U16 | 3 | 1 | 1 | V0.05
6661 | reserved |  |  | U16 |  | 1 | 39 | V0.0B
Setting 영역 시작 | [7 empty] | V0.0B
Communication Settings | [7 empty] | V0.0D
6700 | RS-485 mode 0: slave 1: Master |  |  | U16 | 3,16 | 1 | 1 | V0.0D
6701 | baud rate 0: 9600 1:19200 2:38400 3:57600 4:115200 |  |  | U16 | 3,16 | 1 | 1
6702 | parity 0: none 1: odd 2: even |  |  | U16 | 3,16 | 1 | 1
6703 | device Id |  |  | U16 | 3,16 | 1 | 1
6704 | Eth#0 IP |  |  | U16 | 3,16 | 1 | 4
6708 | Eth#0 SUBNET |  |  | U16 | 3,16 | 1 | 4
6712 | Eth#0 GATEWAY |  |  | U16 | 3,16 | 1 | 4
6716 | Eth#0 DNS |  |  | U16 | 3,16 | 1 | 4
6720 | SNTP IP |  |  | U16 | 3,16 | 1 | 4
6724 | Host Name |  |  | U16 | 3,16 | 1 | 16
6740 | Modbus TCP Port |  |  | U16 | 3,16 | 1 | 1
6741 | DHCP enabled |  |  | U16 | 3,16 | 1 | 1
6742 | GateWay Setting bit 0: gems3500 Meter #1 Enable bit 1: gems3500 Meter #2 Enable bit 2: gems3500 CB #1 Enable bit 3: gems3500 CB #2 Enable bit 4: gems3500 Trip #1 Enable bit 5: gems3500 Trip #2 Enable bit 6: gems3500 ZCT #1 Enable bit 7: gems3500 ZCT #2 Enable |  |  | U16 | 3,16 | 1 | 1
6743 | Onion Server Port, 0이 아니면 서버 동작 |  |  | U16 | 3,16 | 1 | 1 | 6360
6744 |  |  |  | U16 | 3,16 | 1 | 1
6745 |  |  |  | U16 | 3,16 | 1 | 1
6746 | DAQ server ip |  |  | U16 | 3,16 | 1 | 4
6750 | RS485 Master Mode 0: disable 1: Serial Temp Sensor 2: Gateway |  |  | U16 | 3,16 | 1 | 1
6751 | DAQ sampling rate (0: 2k, 1: 4k, 2: 8k, 3: 16k, 4: 32k) |  |  | U16 | 3,16 | 1 | 1
6752 | DAQ sampling buffer length (0: 2k, 1: 4k, 2: 8k, 3: 16k, 4: 32k, 5: 64) |  |  | U16 | 3,16 | 1 | 1
6753 | DAQ interval (minute) |  |  | U16 | 3,16 | 1 | 1
6754 | DAQ format (0: wave, 1: onion) |  |  | U16 | 3,16 | 1 | 1
6755 | DAQ device id |  |  | U16 | 3,16 | 1 | 1 | DAQ setting
6756 | DAQ bitspersample (0: 16bit, 1: 32bit) |  |  | U16 | 3,16 | 1 | 1
6757 | SNTP Mode | 0 : not use, 1 : use |  | U16 |  | 1 | 1
6758 | SNTP Interval |  | min | U16 |  | 1 | 1
6759 |  |  |  | U16 |  | 1 | 1
PT
6760 | wiring mode 0: 3p4w 1: 3p3w(2CT) 2: 3p3w(3CT) 3: 1p2w 4: 1p3w |  |  | U16 | 3,16 | 1 | 1 | V0.08
6761 | Frequency |  |  | U16 | 3,16 | 1 | 1 | V0.08
6762 | V nominal |  |  | U32 | 3,16 | 2 | 1
6764 | PT1 |  |  | U32 | 3,16 | 2 | 1
6766 | PT2 |  |  | U16 | 3,16 | 1 | 1 | 6360
6767 |  |  |  | U16 |  | 1 | 3
CT
6770 | I Nominal |  |  | U16 | 3,16 | 1 | 1
6771 | CT1 |  |  | U16 | 3,16 | 1 | 1
6772 | CT2 0: 5A 1: 100mA/333mV 2: Rogowski |  |  | U16 | 3,16 | 1 | 1
6773 | # turns(unused) |  |  | U16 | 3,16 | 1 | 1
6774 | Starting Current (1.0 : 0.002*In, 0.5: 0.001*In) 0 ~ 10000 (단위 : mA) |  |  | U16 | 3,16 | 1 | 1
6775 | CT1 direction 0: positive 1: negative |  |  | U16 | 3,16 | 1 | 1 | 80
6776 | CT2 direction |  |  | U16 | 3,16 | 1 | 1
6777 | CT3 direction |  |  | U16 | 3,16 | 1 | 1
6778 | Rogowski CT Model |  |  | U16 | 3,16 | 1 | 1
6779 | phase offset 1 * phase resolution 60Hz: 0.0211, 50Hz: 0.0176 * range: +63 ~ -383 1.329 ~ -8.079 1.107 ~ -6.732 |  |  | U16 | 3,16 | 1 | 1
6780 | phase offset 2 |  |  | U16 | 3,16 | 1 | 1
6781 | phase offset 3 |  |  | U16 | 3,16 | 1 | 1
6782 | ZCT Type 1: 200mV:100mV 2: 200mV:1.5mA 3: 200mV:0.1mA |  |  | U16 | 3,16 | 1 | 1
6783 | ZCT Scale |  |  | U16 | 3,16 | 1 | 1
6784 | reserved |  |  | U16 |  | 1 | 6
ETC
6790 | VA type 0: RMS(S=VA) 1: vector(S=sqrt(P*P+Q*Q) |  |  | U16 | 3,16 | 1 | 1
6791 | PF sign 0: IEC 1: IEEE |  |  | U16 | 3,16 | 1 | 1
6792 | demand interval | 0 : 1min, 1:5min, 2:15min, 3:30min, 4:60min |  | U16 | 3,16 | 1 | 1
6793 | Max. Demand for current TDD(A) - unused |  |  | U16 | 3,16 | 1 | 1
6794 | Target Demand (W) |  |  | U32 | 3,16 | 2 | 1
6796 | backlight off time | 0 : always, 1 : 2min, 2 : 4min, 3:6min, 4:8min, 5:10min |  | U16 | 3,16 | 1 | 1
6797 | brightness | 0:20%, 1:40%, 2:60%, 3:80%, 4:100% |  | U16 | 3,16 | 1 | 1
6798 | auto rotation | 0:2sec, 1:4sec, 2:6sec, 3:8sec, 4:10sec |  | U16 | 3,16 | 1 | 1
6799 | Time Zone (~720 ~ 720) | 분단위 |  | S16 | 3,16 | 1 | 1
6800 | max/min reset period | 0: daily 1: weekly 2: monthly 3 : none |  | U16 | 3,16 | 1 | 1
6801 | Test Mode | 0 : normal, 1 : Test mode |  | U16 | 6 | 1 | 1
6802 | (Test Mode)Data update period | 0~65535 | sec | U16 | 6 | 1 | 1
6803 |  |  |  | U16 |  | 1 | 7
PQ Event
6810 | OC Level | 정격의 2배 |  | U16 | 3,16 | 1 | 1 | V0.0C | 일반 metering 데이터만 random data 생성
6811 | OC Cycle | unused |  | U16 | 3,16 | 1 | 1 | V0.0C
6812 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
6813 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
6814 | Event Action (None, Relay) | 0 : none, 1~4 : DO 1~4 |  | U16 | 3,16 | 1 | 1 | 6410
6815 | Sag Level(%), 90% | < 90% |  | U16 | 3,16 | 1 | 1
6816 | Sag Cycle | unused |  | U16 | 3,16 | 1 | 1
6817 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
6818 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1 | V0.08
6819 |  |  |  | U16 | 3,16 | 1 | 1
6820 | Swell Level(%), 110~200~ | > 110% |  | U16 | 3,16 | 1 | 1
6821 | Swell Cycle | unused |  | U16 | 3,16 | 1 | 1
6822 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
6823 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
6824 |  |  |  | U16 | 3,16 | 1 | 1
6825 | Interruption Level, 5% | < 5% |  | U16 | 3,16 | 1 | 1
6826 | Interruption Time, 60s | unused |  | U16 | 3,16 | 1 | 1
6827 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
6828 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
6829 |  |  |  | U16 |  | 1 | 1
Transient Trigger
6830 | Transient Voltage, HoldOff Time, 20ms | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
6831 | Transient Voltage, Absolute Peak Level, 200% | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
6832 | Transient Voltage, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
6833 | Transient Voltage, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
6834 | Transient Current, HoldOff Time | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
6835 | Transient Current, Absolute Peak Level | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
6836 | Transient Current, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
6837 | Transient Current, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
6838 |  |  |  | U16 |  | 1 | 12
Recorder
Waveform
6850 | Recorder resolution(32k, 8k) |  |  | U16 | 3,16 | 1 | 1
6851 | Recorded paramater (U or I) |  |  | U16 | 3,16 | 1 | 1
6852 | pre trigger time(0.1s) |  |  | U16 | 3,16 | 1 | 1
6853 | post trigger time(1s) |  |  | U16 | 3,16 | 1 | 1
Disturbance | [7 empty] | 6450
6854 | Recorder resolution (Half Cycle) |  |  | U16 | 3,16 | 1 | 1
6855 | Recorded parametrs(U or I) |  |  | U16 | 3,16 | 1 | 1
6856 | pre trigger time(100 sample) |  |  | U16 | 3,16 | 1 | 1
6857 | post trigger time(900 sample) |  |  | U16 | 3,16 | 1 | 1
6858 |  |  |  | U16 | 3,16 | 1 | 12
Trend Recorder
6870 | Trend Group #1 Active | 0 : disable, 1 : enable |  | U16 | 3,16 | 1 | 1
6871 | Trend Group #1 Storage Interval | 0 : 1min 1 : 2min 2 : 3min 3 : 5min 4: 10min 5 : 15min 6: 20min 7 : 30min 8 : 60min |  | U16 | 3,16 | 1 | 1
6872 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
6873 | Trend Group #1, Channel #1 |  |  | U16 | 3,16 | 1 | 1
6874 | Trend Group #1, Channel #2 |  |  | U16 | 3,16 | 1 | 1
6875 | Trend Group #1, Channel #3 |  |  | U16 | 3,16 | 1 | 1
6876 | Trend Group #1, Channel #4 |  |  | U16 | 3,16 | 1 | 1
6877 | Trend Group #1, Channel #5 |  |  | U16 | 3,16 | 1 | 1
6878 | Trend Group #1, Channel #6 |  |  | U16 | 3,16 | 1 | 1
6879 | Trend Group #1, Channel #7 |  |  | U16 | 3,16 | 1 | 1
6880 | Trend Group #1, Channel #8 |  |  | U16 | 3,16 | 1 | 1
6881 | Trend Group #1, Channel #9 |  |  | U16 | 3,16 | 1 | 1
6882 | Trend Group #1, Channel #10 |  |  | U16 | 3,16 | 1 | 1
6883 | Trend Group #1, Channel #11 |  |  | U16 | 3,16 | 1 | 1
6884 | Trend Group #1, Channel #12 |  |  | U16 | 3,16 | 1 | 1
6885 | Trend Group #1, Channel #13 |  |  | U16 | 3,16 | 1 | 1
6886 | Trend Group #1, Channel #14 |  |  | U16 | 3,16 | 1 | 1
6887 | Trend Group #1, Channel #15 |  |  | U16 | 3,16 | 1 | 1
6888 | Trend Group #1, Channel #16 |  |  | U16 | 3,16 | 1 | 1
6889 | Trend Group #2 Active |  |  | U16 | 3,16 | 1 | 1
6890 | Trend Group #2 Storage Interval |  |  | U16 | 3,16 | 1 | 1
6891 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1 | 6550
6892 | Trend Group #2, Channel #1 |  |  | U16 | 3,16 | 1 | 1
6893 | Trend Group #2, Channel #2 |  |  | U16 | 3,16 | 1 | 1
6894 | Trend Group #2, Channel #3 |  |  | U16 | 3,16 | 1 | 1
6895 | Trend Group #2, Channel #4 |  |  | U16 | 3,16 | 1 | 1
6896 | Trend Group #2, Channel #5 |  |  | U16 | 3,16 | 1 | 1
6897 | Trend Group #2, Channel #6 |  |  | U16 | 3,16 | 1 | 1
6898 | Trend Group #2, Channel #7 |  |  | U16 | 3,16 | 1 | 1
6899 | Trend Group #2, Channel #8 |  |  | U16 | 3,16 | 1 | 1
6900 | Trend Group #2, Channel #9 |  |  | U16 | 3,16 | 1 | 1
6901 | Trend Group #2, Channel #10 |  |  | U16 | 3,16 | 1 | 1
6902 | Trend Group #2, Channel #11 |  |  | U16 | 3,16 | 1 | 1
6903 | Trend Group #2, Channel #12 |  |  | U16 | 3,16 | 1 | 1
6904 | Trend Group #2, Channel #13 |  |  | U16 | 3,16 | 1 | 1
6905 | Trend Group #2, Channel #14 |  |  | U16 | 3,16 | 1 | 1 | 200
6906 | Trend Group #2, Channel #15 |  |  | U16 | 3,16 | 1 | 1
6907 | Trend Group #2, Channel #16 |  |  | U16 | 3,16 | 1 | 1
6908 | Trend Group #3 Active |  |  | U16 | 3,16 | 1 | 1
6909 | Trend Group #3 Storage Interval |  |  | U16 | 3,16 | 1 | 1
6910 |  |  |  | U16 | 3,16 | 1 | 1
6911 | Trend Group #3, Channel #1 |  |  | U16 | 3,16 | 1 | 1
6912 | Trend Group #3, Channel #2 |  |  | U16 | 3,16 | 1 | 1
6913 | Trend Group #3, Channel #3 |  |  | U16 | 3,16 | 1 | 1
6914 | Trend Group #3, Channel #4 |  |  | U16 | 3,16 | 1 | 1
6915 | Trend Group #3, Channel #5 |  |  | U16 | 3,16 | 1 | 1
6916 | Trend Group #3, Channel #6 |  |  | U16 | 3,16 | 1 | 1
6917 | Trend Group #3, Channel #7 |  |  | U16 | 3,16 | 1 | 1
6918 | Trend Group #3, Channel #8 |  |  | U16 | 3,16 | 1 | 1
6919 | Trend Group #3, Channel #9 |  |  | U16 | 3,16 | 1 | 1
6920 | Trend Group #3, Channel #10 |  |  | U16 | 3,16 | 1 | 1
6921 | Trend Group #3, Channel #11 |  |  | U16 | 3,16 | 1 | 1
6922 | Trend Group #3, Channel #12 |  |  | U16 | 3,16 | 1 | 1
6923 | Trend Group #3, Channel #13 |  |  | U16 | 3,16 | 1 | 1
6924 | Trend Group #3, Channel #14 |  |  | U16 | 3,16 | 1 | 1
6925 | Trend Group #3, Channel #15 |  |  | U16 | 3,16 | 1 | 1
6926 | Trend Group #3, Channel #16 |  |  | U16 | 3,16 | 1 | 1
6927 | Trend Group #4 Active |  |  | U16 | 3,16 | 1 | 1
6928 | Trend Group #4 Storage Interval |  |  | U16 | 3,16 | 1 | 1
6929 |  |  |  | U16 | 3,16 | 1 | 1
6930 | Trend Group #4, Channel #1 |  |  | U16 | 3,16 | 1 | 1
6931 | Trend Group #4, Channel #2 |  |  | U16 | 3,16 | 1 | 1
6932 | Trend Group #4, Channel #3 |  |  | U16 | 3,16 | 1 | 1
6933 | Trend Group #4, Channel #4 |  |  | U16 | 3,16 | 1 | 1
6934 | Trend Group #4, Channel #5 |  |  | U16 | 3,16 | 1 | 1
6935 | Trend Group #4, Channel #6 |  |  | U16 | 3,16 | 1 | 1
6936 | Trend Group #4, Channel #7 |  |  | U16 | 3,16 | 1 | 1
6937 | Trend Group #4, Channel #8 |  |  | U16 | 3,16 | 1 | 1
6938 | Trend Group #4, Channel #9 |  |  | U16 | 3,16 | 1 | 1 | 6760
6939 | Trend Group #4, Channel #10 |  |  | U16 | 3,16 | 1 | 1
6940 | Trend Group #4, Channel #11 |  |  | U16 | 3,16 | 1 | 1
6941 | Trend Group #4, Channel #12 |  |  | U16 | 3,16 | 1 | 1
6942 | Trend Group #4, Channel #13 |  |  | U16 | 3,16 | 1 | 1
6943 | Trend Group #4, Channel #14 |  |  | U16 | 3,16 | 1 | 1
6944 | Trend Group #4, Channel #15 |  |  | U16 | 3,16 | 1 | 1
6945 | Trend Group #4, Channel #16 |  |  | U16 | 3,16 | 1 | 1
6946 |  |  |  | U16 |  | 1 | 4
Power Quality Report
6950 | Active |  |  | U16 | 3,16 | 1 | 1
6951 | Start Day |  |  | U16 | 3,16 | 1 | 1 | 6750
6952 |  |  |  | U16 |  | 1 | 8
Alarm Definition
6960 | compare Time Delay(1s) |  |  | U16 | 3,16 | 1 | 1
6961 |  |  |  | U16 |  | 1 | 1
6962 |  |  |  | U16 |  | 1 | 1
6963 |  |  |  | U16 |  | 1 | 1
Alarm Settings
6964 | Alarm Info #1 Channel(0:disabled, >0: enabled) |  |  | U16 | 3,16 | 1 | 1
6965 | Alarm Cond (0: < , 1:>) |  |  | U16 | 3,16 | 1 | 1
6966 | Hysteresis (% of Nominal) |  |  | U16 | 3,16 | 1 | 1
6967 | Alarm Action (None, Relay) | 0 : none, 1~4 : DO 1~4 |  | U16 | 3,16 | 1 | 1
6968 | Alarm Level |  |  | float | 3,16 | 2 | 1
6970 | Alarm Settings #2 |  |  | U16 | 3,16 | 1 | 6
6976 | Alarm Settings #3 |  |  | U16 | 3,16 | 1 | 6
6982 | Alarm Settings #4 |  |  | U16 | 3,16 | 1 | 6 | V0.08
6988 | Alarm Settings #5 |  |  | U16 | 3,16 | 1 | 6
6994 | Alarm Settings #6 |  |  | U16 | 3,16 | 1 | 6
7000 | Alarm Settings #7 |  |  | U16 | 3,16 | 1 | 6
7006 | Alarm Settings #8 |  |  | U16 | 3,16 | 1 | 6
7012 | Alarm Settings #9 |  |  | U16 | 3,16 | 1 | 6
7018 | Alarm Settings #10 |  |  | U16 | 3,16 | 1 | 6
7024 | Alarm Settings #11 |  |  | U16 | 3,16 | 1 | 6
7030 | Alarm Settings #12 |  |  | U16 | 3,16 | 1 | 6
7036 | Alarm Settings #13 |  |  | U16 | 3,16 | 1 | 6
7042 | Alarm Settings #14 |  |  | U16 | 3,16 | 1 | 6
7048 | Alarm Settings #15 |  |  | U16 | 3,16 | 1 | 6
7054 | Alarm Settings #16 |  |  | U16 | 3,16 | 1 | 6
7060 | Alarm Settings #17 |  |  | U16 | 3,16 | 1 | 6
7066 | Alarm Settings #18 |  |  | U16 | 3,16 | 1 | 6
7072 | Alarm Settings #19 |  |  | U16 | 3,16 | 1 | 6
7078 | Alarm Settings #20 |  |  | U16 | 3,16 | 1 | 6
7084 | Alarm Settings #21 |  |  | U16 | 3,16 | 1 | 6
7090 | Alarm Settings #22 |  |  | U16 | 3,16 | 1 | 6
7096 | Alarm Settings #23 |  |  | U16 | 3,16 | 1 | 6
7102 | Alarm Settings #24 |  |  | U16 | 3,16 | 1 | 6
7108 | Alarm Settings #25 |  |  | U16 | 3,16 | 1 | 6
7114 | Alarm Settings #26 |  |  | U16 | 3,16 | 1 | 6
7120 | Alarm Settings #27 |  |  | U16 | 3,16 | 1 | 6
7126 | Alarm Settings #28 |  |  | U16 | 3,16 | 1 | 6
7132 | Alarm Settings #29 |  |  | U16 | 3,16 | 1 | 6
7138 | Alarm Settings #30 |  |  | U16 | 3,16 | 1 | 6
7144 | Alarm Settings #31 |  |  | U16 | 3,16 | 1 | 6
7150 | Alarm Settings #32 |  |  | U16 | 3,16 | 1 | 6
7156 |  |  |  | U16 |  | 1 | 4
IO Modules #1
7160 | reserved |  |  | U16 |  | 1 | 1
7161 | Module Type | 1 : DI24,DO8,AI8 |  | U16 | 3,16 | 1 | 1
7162 | reserved |  |  | U16 |  | 1 | 2
7164 | UTC Time |  |  | U64 | 3,16 | 4 | 1
7168 | DI TYPE1~32 | 0 : DI, 1 : PI |  | U16 | 3,16 | 1 | 32
7200 | DI debounce 1~32 | 0~255ms | ms | U16 | 3,16 | 1 | 32
7232 | PI Scale 1~32 |  |  | U16 | 3,16 | 1 | 32
7264 | DO TYPE 1~8 | 0 : remote, 1 : alarm, 2 : event |  | U16 | 3,16 | 1 | 8
7272 | DO Output Mode 1~8 | 0 : latch, 1 : pulse |  | U16 | 3,16 | 1 | 8
7280 | DO HoldTime 1~8 | pulse width, 0.1~10s | ms | U16 | 3,16 | 1 | 8
7288 | AI #1 Gain |  |  | float | 3,16 | 2 | 1
7290 | AI #1 Offset |  |  | float | 3,16 | 2 | 1 | V0.0A
7292 | AI #2 Gain |  |  | float | 3,16 | 2 | 1
7294 | AI #2 Offset |  |  | float | 3,16 | 2 | 1
7296 | AI #3 Gain |  |  | float | 3,16 | 2 | 1
7298 | AI #3 Offset |  |  | float | 3,16 | 2 | 1
7300 | AI #4 Gain |  |  | float | 3,16 | 2 | 1
7302 | AI #4 Offset |  |  | float | 3,16 | 2 | 1
7304 | AI #5 Gain |  |  | float | 3,16 | 2 | 1
7306 | AI #5 Offset |  |  | float | 3,16 | 2 | 1
7308 | AI #6 Gain |  |  | float | 3,16 | 2 | 1
7310 | AI #6 Offset |  |  | float | 3,16 | 2 | 1
7312 | AI #7 Gain |  |  | float | 3,16 | 2 | 1
7314 | AI #7 Offset |  |  | float | 3,16 | 2 | 1
7316 | AI #8 Gain |  |  | float | 3,16 | 2 | 1
7318 | AI #8 Offset |  |  | float | 3,16 | 2 | 1
7320 | DCI#1, Shunt Type | 0 : 50mV, 1 : 60mV, 2 : 100mV |  | U16 | 3,16 | 1 | 1
7321 | DCI#1, Nominal Current |  |  | U16 | 3,16 | 1 | 1
7322 | DCI#2, Shunt Type |  |  | U16 | 3,16 | 1 | 1
7323 | DCI#2, Nominal Current |  |  | U16 | 3,16 | 1 | 1
7324 | DCI#3, Shunt Type |  |  | U16 | 3,16 | 1 | 1
7325 | DCI#3, Nominal Current |  |  | U16 | 3,16 | 1 | 1
7326 | DCI#4, Shunt Type |  |  | U16 | 3,16 | 1 | 1
7327 | DCI#4, Nominal Current |  |  | U16 | 3,16 | 1 | 1
7328 | reserved |  |  | U16 | 3,16 | 1 | 12
7340 | UTC Time |  |  | U16 | 3,16 | 1 | 4
7344 | reserved |  |  | U16 | 3,16 | 1 | 6
Command
7350 | reboot |  |  | U16 | 6 | 1 | 1
7351 | save settings |  |  | U16 | 6 | 1 | 1
7352 | Calibration command 0: Enable Calibration 1: U gain 2: I gain 3: W gain 4: Ph gain 5: clear V 6: clear I 7: clear W 8: clear phase 9: IN gain 10: clear IN 11: Disable Calibration 12: save Calibration 13: Upp gain 14: clear Upp gain 15: set dcos 16: clear DcOffset 17: --- 18: --- |  |  | U16 | 6 | 1 | 1
7353 | V-ref, 1=1V |  |  | U16 | 6 | 1 | 1
7354 | I-ref, 1=0.1A |  |  | U16 | 6 | 1 | 1 | 2020.3.13
7355 | clear demand |  |  | U16 | 6 | 1 | 1 | 2020.3.13
7356 | clear minmax |  |  | U16 | 6 | 1 | 1
7357 | clear energy |  |  | U16 | 6 | 1 | 1
7358 | clear alarm |  |  | U16 | 6 | 1 | 1
7359 | init settings |  |  | U16 | 6 | 1 | 1
7360 | clear event |  |  | U16 | 6 | 1 | 1
7361 | In-ref, 1=0.1 |  |  | U16 | 6 | 1 | 1
7362 | Alarm Ack - DO Reset |  |  | U16 | 6 | 1 | 1
7363 | DAQ enable |  |  | U16 | 6 | 1 | 1
7364 | clear ITIC |  |  | U16 | 6 | 1 | 1
7365 | Event Ack - DO Reset |  |  | U16 | 6 | 1 | 1
7366 | clear PI |  |  | U16 | 6 | 1 | 1 | V0.09
7367 | reserved |  |  | U16 | 6 | 1 | 1
7368 |  |  |  | U16 | 6 | 1 | 1
7369 |  |  |  | U16 | 6 | 1 | 1
7370 | load event | 1: down, 2:up, 3:top |  | U16 | 6 | 1 | 1 | 2025-03-17
7371 | load alarm | 1: down, 2:up, 3:top |  | U16 | 6 | 1 | 1 | 2025-03-17
7372 | load itic | 1: down, 2:up, 3:top |  | U16 | 6 | 1 | 1 | 2025-03-17
7373 |  |  |  | U16 | 6 | 1 | 1
7374 |  |  |  | U16 | 6 | 1 | 1
7375 |  |  |  | U16 | 6 | 1 | 1
7376 |  |  |  | U16 | 6 | 1 | 1
7377 |  |  |  | U16 | 6 | 1 | 1
7378 |  |  |  | U16 | 6 | 1 | 1
7379 |  |  |  | U16 | 6 | 1 | 1
7380 |  |  |  | U16 | 6 | 1 | 20
ITIC | [7 empty] | V0.09
7400 | fr |  |  | U16 | 3 | 1 | 1 | V0.08
7401 | re |  |  | U16 | 3 | 1 | 1 | V0.0C
7402 | count |  |  | U16 | 3 | 1 | 1
7403 | reserved |  |  | U16 | 3 | 1 | 1
7404 | Log #1 | start ts |  | UTC | 3 | 2 | 1
7406 |  | start ts(ms) |  | U16 | 3 | 1 | 1
7407 |  | duration |  | U16 | 3 | 1 | 1
7408 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
7409 |  | mask |  | U16 | 3 | 1 | 1
7410 |  | Level 1 |  | float | 3 | 2 | 1
7412 |  | Level 2 |  | float | 3 | 2 | 1
7414 |  | Level 3 |  | float | 3 | 2 | 1
7416 |  | Normal |  | float | 3 | 2 | 1
7418 | Log #2 |  |  | U16 | 3 | 1 | 14 | 2025-03-17
7432 | Log #3 |  |  | U16 | 3 | 1 | 14
7446 | Log #4 |  |  | U16 | 3 | 1 | 14
7460 | Log #5 |  |  | U16 | 3 | 1 | 14
7474 | Log #6 |  |  | U16 | 3 | 1 | 14
7488 | Log #7 |  |  | U16 | 3 | 1 | 14
7502 | Log #8 |  |  | U16 | 3 | 1 | 14
7516 | Log #9 |  |  | U16 | 3 | 1 | 14
7530 | Log #10 |  |  | U16 | 3 | 1 | 14
7544 | Log #11 |  |  | U16 | 3 | 1 | 14
7558 | Log #12 |  |  | U16 | 3 | 1 | 14
7572 | Log #13 |  |  | U16 | 3 | 1 | 14
7586 | Log #14 |  |  | U16 | 3 | 1 | 14
7600 | Log #15 |  |  | U16 | 3 | 1 | 14
7614 | Log #16 |  |  | U16 | 3 | 1 | 14
7628 | Log #17 |  |  | U16 | 3 | 1 | 14
7642 | Log #18 |  |  | U16 | 3 | 1 | 14
7656 | Log #19 |  |  | U16 | 3 | 1 | 14
7670 | Log #20 |  |  | U16 | 3 | 1 | 14
7684 | Log #21 |  |  | U16 | 3 | 1 | 14
7698 | Log #22 |  |  | U16 | 3 | 1 | 14
7712 | Log #23 |  |  | U16 | 3 | 1 | 14
7726 | Log #24 |  |  | U16 | 3 | 1 | 14
7740 | Log #25 |  |  | U16 | 3 | 1 | 14
7754 | Log #26 |  |  | U16 | 3 | 1 | 14
7768 | Log #27 |  |  | U16 | 3 | 1 | 14
7782 | Log #28 |  |  | U16 | 3 | 1 | 14
7796 | Log #29 |  |  | U16 | 3 | 1 | 14
7810 | Log #30 |  |  | U16 | 3 | 1 | 14
7824 | Log #31 |  |  | U16 | 3 | 1 | 14
7838 | Log #32 |  |  | U16 | 3 | 1 | 14
7852 |  |  |  | U16 | 3 | 1 | 148 | 452
8000 |  |  |  | U16 | 3 | 1 | 2000
10000

## Alarm Channel
Trend/Alarm Channel
1 | Temp
2 | Freq | uder/over
3 | U1 | uder/over
4 | U2 | uder/over
5 | U3 | uder/over
6 | U~
7 | U12
8 | U23
9 | U31
10 | Upp~
11 | Voltage Unbalace, Uo
12 | Voltage Unbalace, Uu
13 | I1
14 | I2
15 | I3
16 | I~
17 | Itotal
18 | In
19 | P1 | reverse
20 | P2 | reverse
21 | P3 | reverse
22 | Ptotal
23 | Q1
24 | Q2
25 | Q3
26 | Qtot
27 | D1
28 | D2
29 | D3
30 | D
31 | S1
32 | S2
33 | S3
34 | Stot
35 | PF1
36 | PF2
37 | PF3
38 | PFtot
39 | THD U1
40 | THD U2
41 | THD U3
42 | THD U12
43 | THD U23
44 | THD U31
45 | THD I1
46 | THD I2
47 | THD I3
48 | Dynamic Demand P+
49 | Dynamic Demand P-
50 | Dynamic Demand Q+
51 | Dynamic Demand Q-
52 | Dynamic Demand S
53 | Dynamic Demand I1
54 | Dynamic Demand I2
55 | Dynamic Demand I3
56 | Max. Demand P+
57 | Max. Demand P=-
58 | Max. Demand Q+
59 | Max. Demand Q-
60 | Max. Demand S
61 | Max. Demand I1
62 | Max. Demand I2
63 | Max. Demand I3
64 | Iunbalance2
65 | Iunbalance0
66 | Summary
67 | DI #1
68 | DI #2
69 | DI #3
70 | DI #4
71 | DI #5
72 | DI #6
73 | DI #7
74 | DI #8
75 | DO #1
76 | DO #2
77 | #1 iPSM72 comm
78 | #1 iPSM72 DI(Outgoing MCB Trip)
79 | #1 iPSM72 DO
80 | #1 iPSM72 IG(Earth Leakage)
81 | #1 iPSM72 R Swell
82 | #1 iPSM72 S Swell
83 | #1 iPSM72 T Swell
84 | #1 iPSM72 R Sag
85 | #1 iPSM72 S Sag
86 | #1 iPSM72 T Sag
87 | #2 iPSM72 comm
88 | #2 iPSM72 DI(Outgoing MCB Trip)
89 | #2 iPSM72 DO
90 | #2 iPSM72 IG(Earth Leakage)
91 | #2 iPSM72 R Swell
92 | #2 iPSM72 S Swell
93 | #2 iPSM72 T Swell
94 | #2 iPSM72 R Sag
95 | #2 iPSM72 S Sag
96 | #2 iPSM72 T Sag
97 | Under Deviation U1
98 | Under Deviation U2
99 | Under Deviation U3
100 | Over Drviation U1
101 | Over Drviation U2
102 | Over Drviation U3
103 | CF U1
104 | CF U2
105 | CF U3
106 | CF U12
107 | CF U23
108 | CF U31
109 | CF I1
110 | CF I2
111 | CF I3
112 | KF I1
113 | KF I2
114 | KF I3
115 | PSt 1
116 | PSt 2
117 | PSt 3
118 | Plt 1
119 | Plt 2
120 | Plt 3
121 | Sig. Volt 1
122 | Sig. Volt 2
123 | Sig. Volt 3

## IOM
Address | Name | 설명 | Unit | Type | FC | Word Count | Item Count
Data
0 | hbeat | 100ms ++ |  | U16 | 3 | 1 | 1
1 | type | 1 : DIO#1 2 : CT#1 |  | U16 | 3 | 1 | 1
2 | dbflag | database download flag |  | U16 | 3 | 1 | 1 | iom 재기동시 1 set
3 | subtype |  |  | U16 | 3 | 1 | 1
4 | DI 0~31 | DI 상태 |  | U16 | 3 | 1 | 32
36 | PI 0~31 | PI 상태 |  | U16 | 3 | 1 | 32
68 | DO 0~7 |  |  | U16 | 3,6 | 1 | 8
76 | AI 0~7 |  |  | float | 3 | 2 | 8
92 | DC V |  |  | float | 3 | 2 | 1
94 | DC I1 |  |  | float | 3 | 2 | 1
96 | DC I2 |  |  | float | 3 | 2 | 1
98 | reserved |  |  | U16 | 3 | 1 | 2
SOE CNT
100 | SOE Count | SOE Count, Dump 후 clear |  | U16 | 3 | 1 | 1
101 | reserved |  |  | U16 | 3 | 1 | 3
SOE
104 | Time Stamp | #0 |  | TS | 3 | 4 | 1
108 | DI Status |  |  | U16 | 3 | 1 | 1
109 | DI pnt |  |  | U16 | 3 | 1 | 1
110 | reserved |  |  | U16 | 3 | 1 | 2
112 |  | #1 |  |  | 3 | 1 | 8
120 |  | #2 |  |  | 3 | 1 | 8
128 |  | #3 |  |  | 3 | 1 | 8
136 |  | #4 |  |  | 3 | 1 | 8
144 |  | #5 |  |  | 3 | 1 | 8
152 |  | #6 |  |  | 3 | 1 | 8
160 |  | #7 |  |  | 3 | 1 | 8
168 |  | #8 |  |  | 3 | 1 | 8
176 |  | #9 |  |  | 3 | 1 | 8
184 |  | #10 |  |  | 3 | 1 | 8
192 |  | #11 |  |  | 3 | 1 | 8
200 |  | #12 |  |  | 3 | 1 | 8
208 |  | #13 |  |  | 3 | 1 | 8
216 |  | #14 |  |  | 3 | 1 | 8
224 |  | #15 |  |  | 3 | 1 | 8
Setting
232 | Enable |  |  | U16 | 3,16 | 1 | 1
233 | Module Type |  |  | U16 | 3,16 | 1 | 1
234 | reserved |  |  | U16 | 3,16 | 1 | 2
236 | UTC Time |  |  | TS | 3,16 | 4 | 1
240 | DI TYPE1~32 | (0=state, 1=pulse) |  | U16 | 3,16 | 1 | 32
272 | DI debounce 1~32 | 0~255 |  | U16 | 3,16 | 1 | 32
304 | PI Scale 1~32 | 1 ~ 65535 |  | U16 | 3,16 | 1 | 32
336 | DO TYPE 1~8 | (0=Relay, 1=alarm) |  | U16 | 3,16 | 1 | 8
344 | DO Output Mode 1~8 | 0: Latch type, 아니면 On Timer |  | U16 | 3,16 | 1 | 8
352 | DO HoldTime 1~8 |  |  | U16 | 3,16 | 1 | 8
360 | AI #1 Gain |  |  | float | 3,16 | 2 | 1
362 | AI #1 Offset |  |  | float | 3,16 | 2 | 1
364 | AI #2 Gain |  |  | float | 3,16 | 2 | 1
366 | AI #2 Offset |  |  | float | 3,16 | 2 | 1
368 | AI #3 Gain |  |  | float | 3,16 | 2 | 1
370 | AI #3 Offset |  |  | float | 3,16 | 2 | 1
372 | AI #4 Gain |  |  | float | 3,16 | 2 | 1
374 | AI #4 Offset |  |  | float | 3,16 | 2 | 1
376 | AI #5 Gain |  |  | float | 3,16 | 2 | 1
378 | AI #5 Offset |  |  | float | 3,16 | 2 | 1
380 | AI #6 Gain |  |  | float | 3,16 | 2 | 1
382 | AI #6 Offset |  |  | float | 3,16 | 2 | 1
384 | AI #7 Gain |  |  | float | 3,16 | 2 | 1
386 | AI #7 Offset |  |  | float | 3,16 | 2 | 1
388 | AI #8 Gain |  |  | float | 3,16 | 2 | 1
390 | AI #8 Offset |  |  | float | 3,16 | 2 | 1
392 | DCI#1, Shunt Type |  |  | U16 | 3,16 | 1 | 1
393 | DCI#1, Nominal Current |  |  | U16 | 3,16 | 1 | 1
394 | DCI#2, Shunt Type |  |  | U16 | 3,16 | 1 | 1
395 | DCI#2, Nominal Current |  |  | U16 | 3,16 | 1 | 1
396 | DCI#3, Shunt Type |  |  | U16 | 3,16 | 1 | 1
397 | DCI#3, Nominal Current |  |  | U16 | 3,16 | 1 | 1
398 | DCI#4, Shunt Type |  |  | U16 | 3,16 | 1 | 1
399 | DCI#4, Nominal Current |  |  | U16 | 3,16 | 1 | 1
Command
400 | reset |  |  | U16 | 6 | 1 | 1
401 | clear PI value |  |  | U16 | 6 | 1 | 1