## ToDo&Log
2024-12-18 | 1st draft
2026-06-02 | 3ch redefine
2026-06-02
2026-06-02
2026-06-02
2026-06-02
2026-06-02
2026-06-02
2026-06-02
2026-06-02
2026-06-02
2026-06-02
2026-06-02
2026-06-02
2026-06-02
2026-06-02
2026-06-02

## #1,2,3 Simple
address | Group | name | Decription | 1P | 3P | Unit | Function code | TYPE | 1P | 3P | Word Count | Item Count
Metering
7000 | Common | Time Stamp |  |  |  |  | 3,4 | U32 |  |  | 2 | 1
7002 |  | Heatbit |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
7003 |  | HW Model |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
7004 |  | HW Version |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
7005 |  | FW Version |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
7006 |  | FW_BUILD_YEAR |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
7007 |  | FW_BUILD_MON |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
7008 |  | FW_BUILD_DAY |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
7009 |  | Serial Num |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
7010 |  | Status |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
7011 |  | reserved |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
7012 |  | Internal Temp |  |  |  |  | 3,4 | float |  |  | 2 | 1
7014 |  | reserved |  |  |  |  | 3,4 | U32 |  |  | 2 | 3
7020 | #1 | CB Type |  | ● | ● |  | 3,4 | U16 |  |  | 1 | 1
7021 |  | CB Status |  | ● | ● |  | 3,4 | U16 |  |  | 1 | 1
7022 |  | reserved |  | ● | ● |  | 3,4 | U32 |  |  | 2 | 1
7024 |  | Frequency |  | ● | ● | Hz | 3,4 | float |  |  | 2 | 1
7026 |  | U1 | 상전압 1 | ● | ● | V | 3,4 | float |  |  | 2 | 1
7028 |  | U2 | 상전압 2 |  | ● |  | 3,4 | float |  |  | 2 | 1
7030 |  | U3 | 상전압 3 |  | ● |  | 3,4 | float |  |  | 2 | 1
7032 |  | U12 |  |  | ● |  | 3,4 | float |  |  | 2 | 1
7034 |  | U23 |  |  | ● |  | 3,4 | float |  |  | 2 | 1
7036 |  | U31 |  |  | ● |  | 3,4 | float |  |  | 2 | 1
7038 |  | I1 | 상전류 1 | ● | ● | A | 3,4 | float |  |  | 2 | 1
7040 |  | I2 | 상전류 2 |  | ● |  | 3,4 | float |  |  | 2 | 1
7042 |  | I3 | 상전류 3 |  | ● |  | 3,4 | float |  |  | 2 | 1
7044 |  | In | 누설전류 |  | ● |  | 3,4 | float |  |  | 2 | 1
7046 |  | P1 |  | ● | ● | W | 3,4 | float |  |  | 2 | 1
7048 |  | P2 |  |  | ● |  | 3,4 | float |  |  | 2 | 1
7050 |  | P3 |  |  | ● |  | 3,4 | float |  |  | 2 | 1
7052 |  | P total |  | ● | ● |  | 3,4 | float |  |  | 2 | 1
7054 |  | Q total |  | ● | ● | Var | 3,4 | float |  |  | 2 | 1
7056 |  | S total |  | ● | ● | VA | 3,4 | float |  |  | 2 | 1
7058 |  | PF total |  | ● | ● | % | 3,4 | float |  |  | 2 | 1
7060 |  | kWh_imp |  | ● | ● | kWh | 3,4 | U32 |  |  | 2 | 1
7062 |  | kWh_imp_this_month |  | ● | ● | kWh | 3,4 | U32 |  |  | 2 | 1
7064 |  | kWh_imp_last_month |  | ● | ● | kWh | 3,4 | U32 |  |  | 2 | 1
7066 |  | kVARh_imp |  | ● | ● | kVarh | 3,4 | U32 |  |  | 2 | 1
7068 |  | kVAh |  | ● | ● | kVAh | 3,4 | U32 |  |  | 2 | 1
7070 |  | Volt. Unbalance |  | ● | ● | % | 3,4 | float |  |  | 2 | 1
7072 |  | Current Unbalance |  | ● | ● | % | 3,4 | float |  |  | 2 | 1
7074 |  | THD V1 | 고조파함유율 상전압 1 | ● | ● | % | 3,4 | float |  |  | 2 | 1
7076 |  | THD V2 | 고조파함유율 상전압 2 |  | ● | % | 3,4 | float |  |  | 2 | 1
7078 |  | THD V3 | 고조파함유율 상전압 3 |  | ● | % | 3,4 | float |  |  | 2 | 1
7080 |  | THD I1 | 고조파함유율 상전류 1 | ● | ● | % | 3,4 | float |  |  | 2 | 1
7082 |  | THD I2 | 고조파함유율 상전류 2 |  | ● | % | 3,4 | float |  |  | 2 | 1
7084 |  | THD I3 | 고조파함유율 상전류 3 |  | ● | % | 3,4 | float |  |  | 2 | 1
7086 |  | TDD I1 | 디맨드왜형율 상전류 1 | ● | ● | % | 3,4 | float |  |  | 2 | 1
7088 |  | TDD I2 | 디맨드왜형율 상전류 2 |  | ● | % | 3,4 | float |  |  | 2 | 1
7090 |  | TDD I3 | 디맨드왜형율 상전류 3 |  | ● | % | 3,4 | float |  |  | 2 | 1
7092 |  | reserved |  | ● | ● |  | 3,4 | float |  |  | 2 | 4
7100 | #2 |  |  | ● | ● |  | 3,4 | float |  |  | 1 | 80
7180 | #3 |  |  | ● | ● |  | 3,4 | float |  |  | 1 | 80
7260 | #4 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
7340 | #5 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
7420 | #6 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
7500 | #7 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
7580 | #8 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
7660 | #9 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
Harmonics by order
7740 | #1 | Harmonics V1 | 1~41th | ● | ● |  | 3,4 | S16 |  |  | 1 | 41
7781 |  | Harmonics V2 |  |  | ● |  | 3,4 | S16 |  |  | 1 | 41
7822 |  | Harmonics V3 |  |  | ● |  | 3,4 | S16 |  |  | 1 | 41
7863 |  | Harmonics I1 |  | ● | ● |  | 3,4 | S16 |  |  | 1 | 41
7904 |  | Harmonics I2 |  |  | ● |  | 3,4 | S16 |  |  | 1 | 41
7945 |  | Harmonics I3 |  |  | ● |  | 3,4 | S16 |  |  | 1 | 41
7986 | #2 |  |  | ● | ● | [5 empty] | 1 | 246
8232 | #3 |  |  | ● | ● | [5 empty] | 1 | 246
8478 | #4 |  |  | ● | [6 empty] | 1 | 246
8724 | #5 |  |  | ● | [6 empty] | 1 | 246
8970 | #6 |  |  | ● | [6 empty] | 1 | 246
9216 | #7 |  |  | ● | [6 empty] | 1 | 246
9462 | #8 |  |  | ● | [6 empty] | 1 | 246
9708 | #9 |  |  | ● | [6 empty] | 1 | 246

## #1CH modbus
address | name | 설명 | Unit | TYPE | FC | Word Count | Item Count
Metering | [7 empty] | 구현
0 | Time Stamp |  |  | UTC | 3 | 2 | 1
2 | TYPE |  |  | U16 | 3 | 1 | 1
3 | STATUS | 1 : online, 0 : offline |  | U16 | 3 | 1 | 1
4 | Frequency | 라인주파수 | Hz | float | 3 | 2 | 1
6 | Internal Temp |  | ℃ | float | 3 | 2 | 1
8 | U1 | 상전압 1 | V | float | 3 | 2 | 1
10 | U2 | 상전압 2 |  | float | 3 | 2 | 1
12 | U3 | 상전압 3 |  | float | 3 | 2 | 1
14 | U~ | 상전압 평균 |  | float | 3 | 2 | 1
16 | U12 | 선간 전압 12 |  | float | 3 | 2 | 1
18 | U23 | 선간 전압 23 |  | float | 3 | 2 | 1
20 | U31 | 선간 전압 31 |  | float | 3 | 2 | 1
22 | Upp~ | 선간 전압 평균 |  | float | 3 | 2 | 1
24 | Uunbalance2 |  | % | float | 3 | 2 | 1 |  | Uu=neg/pos*100
26 | Uunbalance0 |  |  | float | 3 | 2 | 1 |  | Uo=zero/pos*100
28 | U Zero Sequence Mag. |  |  | float | 3 | 2 | 1
30 | U Zero Sequence angle |  |  | float | 3 | 2 | 1
32 | U Positive Sequence Mag. |  |  | float | 3 | 2 | 1
34 | U Positive Sequence angle |  |  | float | 3 | 2 | 1
36 | U Negative Sequence Mag |  |  | float | 3 | 2 | 1
38 | U Negative Sequence angle |  |  | float | 3 | 2 | 1
40 | Angle U1 |  |  | float | 3 | 2 | 1
42 | Angle U2 |  |  | float | 3 | 2 | 1
44 | Angle U3 |  |  | float | 3 | 2 | 1
46 | U Underdeviation L1 |  | % | float | 3 | 2 | 1
48 | U Underdeviation L2 |  | % | float | 3 | 2 | 1
50 | U Underdeviation L3 |  | % | float | 3 | 2 | 1
52 | U Overdeviation L1 |  | % | float | 3 | 2 | 1
54 | U Overdeviation L2 |  | % | float | 3 | 2 | 1
56 | U Overdeviation L3 |  | % | float | 3 | 2 | 1
58 | I1 | 상전류 1 | A | float | 3 | 2 | 1
60 | I2 | 상전류 2 |  | float | 3 | 2 | 1
62 | I3 | 상전류 3 |  | float | 3 | 2 | 1
64 | I~ |  |  | float | 3 | 2 | 1
66 | I total (I1+I2+I3) |  |  | float | 3 | 2 | 1
68 | In(Measured) |  |  | float | 3 | 2 | 1 |  | 1. 5A: -3P4W(In) -3P3W(Ig), 2. AT/VT: Ig로 사용
70 | In(Calculated) | Ia+Ib+Ic+In = Ig |  | float | 3 | 2 | 1 |  | 1. 5A: -3P4W(Ig=Ia+Ib+Ic+In), -3P3W(Ig=Ia+Ib+Ic), 2. AT/VT: 5A와 동일
72 | Ig |  |  | float | 3 | 2 | 1
74 | I Zero Sequence Mag |  |  | float | 3 | 2 | 1
76 | I Zero Sequence angle |  |  | float | 3 | 2 | 1
78 | I Positive Sequence Mag. |  |  | float | 3 | 2 | 1
80 | I Positive Sequence angle |  |  | float | 3 | 2 | 1
82 | I Negative Sequence Mag. |  |  | float | 3 | 2 | 1
84 | I Negative Sequence angle |  |  | float | 3 | 2 | 1
86 | Angle I1 |  |  | float | 3 | 2 | 1
88 | Angle I2 |  |  | float | 3 | 2 | 1
90 | Angle I3 |  |  | float | 3 | 2 | 1
92 | Iunbalance2 |  | % | float | 3 | 2 | 1
94 | Iunbalance0 |  |  | float | 3 | 2 | 1
96 | P1 | 유효전력 P1 | W | float | 3 | 2 | 1
98 | P2 | 유효전력 P2 |  | float | 3 | 2 | 1
100 | P3 | 유효전력 P3 |  | float | 3 | 2 | 1
102 | P total | 유효전력 P-total |  | float | 3 | 2 | 1
104 | fP1 |  |  | float | 3 | 2 | 1
106 | fP2 |  |  | float | 3 | 2 | 1
108 | fP3 |  |  | float | 3 | 2 | 1
110 | fP total |  |  | float | 3 | 2 | 1
112 | Q1 | 무효전력 Q1 | VAR | float | 3 | 2 | 1
114 | Q2 | 무효전력 Q2 |  | float | 3 | 2 | 1
116 | Q3 | 무효전력 Q3 |  | float | 3 | 2 | 1
118 | Q total | 무효전력 Q-total |  | float | 3 | 2 | 1
120 | fQ1 |  |  | float | 3 | 2 | 1
122 | fQ2 |  |  | float | 3 | 2 | 1
124 | fQ3 |  |  | float | 3 | 2 | 1
126 | fQ total |  |  | float | 3 | 2 | 1
128 | S1 | 피상전력 S1 | VA | float | 3 | 2 | 1
130 | S2 | 피상전력 S2 |  | float | 3 | 2 | 1
132 | S3 | 피상전력 S3 |  | float | 3 | 2 | 1
134 | S total | 피상전력 S-total |  | float | 3 | 2 | 1
136 | fS1 |  |  | float | 3 | 2 | 1
138 | fS2 |  |  | float | 3 | 2 | 1
140 | fS3 |  |  | float | 3 | 2 | 1
142 | fS total |  |  | float | 3 | 2 | 1
144 | PF1 | 역률 PF1 | % | float | 3 | 2 | 1
146 | PF2 | 역률 PF2 |  | float | 3 | 2 | 1
148 | PF3 | 역률 PF3 |  | float | 3 | 2 | 1
150 | PF total | 역률 PF-total |  | float | 3 | 2 | 1
152 | dPF1 |  | % | float | 3 | 2 | 1
154 | dPF2 |  |  | float | 3 | 2 | 1
156 | dPF3 |  |  | float | 3 | 2 | 1
158 | dPF total |  |  | float | 3 | 2 | 1
160 | deformed Power D L1 |  | W | float | 3 | 2 | 1 |  | S=sqrt {P^{2}+Q^{2}+D^{2}}
162 | deformed Power D L2 |  |  | float | 3 | 2 | 1
164 | deformed Power D L3 |  |  | float | 3 | 2 | 1
166 | deformed Power D Total |  |  | float | 3 | 2 | 1
168 | Power Angle(atan(fPt,fQt) L1 |  | Degree | float | 3 | 2 | 1 |  | Angle between fundamental phase voltage and phase current
170 | Power Angle(atan(fPt,fQt) L2 |  |  | float | 3 | 2 | 1
172 | Power Angle(atan(fPt,fQt) L3 |  |  | float | 3 | 2 | 1
174 |  |  |  | float | 3 | 2 | 1
176 | THD V1 |  | % | float | 3 | 2 | 1
178 | THD V2 |  |  | float | 3 | 2 | 1 |  | Chip에서 제공하는 결과 사용
180 | THD V3 |  |  | float | 3 | 2 | 1
182 | THD V12 |  |  | float | 3 | 2 | 1
184 | THD V23 |  |  | float | 3 | 2 | 1
186 | THD V31 |  |  | float | 3 | 2 | 1
188 | CF V1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
190 | CF V2 |  |  | float | 3 | 2 | 1
192 | CF V3 |  |  | float | 3 | 2 | 1
194 | CF V12 |  |  | float | 3 | 2 | 1
196 | CF V23 |  |  | float | 3 | 2 | 1
198 | CF V31 |  |  | float | 3 | 2 | 1
200 | THD I1 |  |  | float | 3 | 2 | 1
202 | THD I2 |  |  | float | 3 | 2 | 1
204 | THD I3 |  |  | float | 3 | 2 | 1
206 | TDD I1 |  |  | float | 3 | 2 | 1
208 | TDD I2 |  |  | float | 3 | 2 | 1
210 | TDD I3 |  |  | float | 3 | 2 | 1
212 | K I1 | K-FACTOR : 고조파 허용율 |  | float | 3 | 2 | 1
214 | K I2 |  |  | float | 3 | 2 | 1
216 | K I3 |  |  | float | 3 | 2 | 1
218 | CF I1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
220 | CF I2 |  |  | float | 3 | 2 | 1
222 | CF I3 |  |  | float | 3 | 2 | 1
224 | fU1 | 기본파 U1 | V | float | 3 | 2 | 1
226 | fU2 | 기본파 U2 |  | float | 3 | 2 | 1
228 | fU3 | 기본파 U3 |  | float | 3 | 2 | 1
230 | fU~ | 기본파 전압 평균 |  | float | 3 | 2 | 1
232 | fI1 | 기본파 I1 | A | float | 3 | 2 | 1
234 | fI2 | 기본파 I2 |  | float | 3 | 2 | 1
236 | fI3 | 기본파 I3 |  | float | 3 | 2 | 1
238 | fI~ | 기본파 전류 평균 |  | float | 3 | 2 | 1
Energy
240 | import kwh(0 ~ 999,999,999.9 kw) | 누적 유효전력량 |  | U32 | 3 | 2 | 1
242 | export kwh |  |  | U32 | 3 | 2 | 1
244 | import kvarh |  |  | U32 | 3 | 2 | 1
246 | export kvarh |  |  | U32 | 3 | 2 | 1
248 | kvah |  |  | U32 | 3 | 2 | 1
250 |  |  |  | U32 | 3 | 2 | 1
252 | import kwh this month |  |  | U32 | 3 | 2 | 1
254 | export kwh this month |  |  | U32 | 3 | 2 | 1
256 | import kvarh this month |  |  | U32 | 3 | 2 | 1
258 | export kvarh this month |  |  | U32 | 3 | 2 | 1
260 | kvah this month |  |  | U32 | 3 | 2 | 1
262 |  |  |  | U32 | 3 | 2 | 1
264 | import kwh last month |  |  | U32 | 3 | 2 | 1 |  | Demand P(import)
266 | export kwh last month |  |  | U32 | 3 | 2 | 1
268 | import kvarh last month |  |  | U32 | 3 | 2 | 1
270 | export kvarh last month |  |  | U32 | 3 | 2 | 1
272 | kvah last month |  |  | U32 | 3 | 2 | 1
274 |  |  |  | U32 | 3 | 2 | 1
276 | import kwh | 0~999,999,999.999 kw |  | U64 | 3 | 4 | 1 |  | Demand P(import)
280 | export kwh |  |  | U64 | 3 | 4 | 1
284 | import kvarh |  |  | U64 | 3 | 4 | 1
288 | export kvarh |  |  | U64 | 3 | 4 | 1
292 | kvah |  |  | U64 | 3 | 4 | 1
296 |  |  |  | U64 | 3 | 4 | 1
Demand
300 | Time Stamp |  |  | UTC | 3 | 2 | 1
302 | Max Demand P(import) |  |  | float | 3 | 2 | 1
304 | Time Stamp |  |  | UTC | 3 | 2 | 1
306 | Max Demand P(export) |  |  | float | 3 | 2 | 1
308 | Time Stamp |  |  | UTC | 3 | 2 | 1
310 | Max Demand Q(import) |  |  | float | 3 | 2 | 1
312 | Time Stamp |  |  | UTC | 3 | 2 | 1
314 | Max Demand Q(export) |  |  | float | 3 | 2 | 1
316 | Time Stamp |  |  | UTC | 3 | 2 | 1
318 | Max Demand S |  |  | float | 3 | 2 | 1
320 | Time Stamp |  |  | UTC | 3 | 2 | 1
322 | Max Demand I1 |  |  | float | 3 | 2 | 1
324 | Time Stamp |  |  | UTC | 3 | 2 | 1
326 | Max Demand I2 |  |  | float | 3 | 2 | 1
328 | Time Stamp |  |  | UTC | 3 | 2 | 1
330 | Max Demand I3 |  |  | float | 3 | 2 | 1
332 | Demand time stamp |  |  | UTC | 3 | 2 | 1
334 | Demand P(import) |  |  | float | 3 | 2 | 1
336 | Demand P(export) |  |  | float | 3 | 2 | 1 |  | 최근 24시간 그래프 그린다
338 | Demand Q(import) |  |  | float | 3 | 2 | 1
340 | Demand Q(export) |  |  | float | 3 | 2 | 1
342 | Demand S(export) |  |  | float | 3 | 2 | 1
344 | Demand I1 |  |  | float | 3 | 2 | 1
346 | Demand I2 |  |  | float | 3 | 2 | 1
348 | Demand I3 |  |  | float | 3 | 2 | 1
350 | Present Demand P(import) |  |  | float | 3 | 2 | 1
352 | Present Demand P(export) |  |  | float | 3 | 2 | 1
354 | Present Demand Q(import) |  |  | float | 3 | 2 | 1
356 | Present Demand Q(export) |  |  | float | 3 | 2 | 1
358 | Present Demand S(export) |  |  | float | 3 | 2 | 1
360 | Forecast Demand P(export) |  |  | float | 3 | 2 | 1
362 | Demand P 15m(import) |  |  | float | 3 | 2 | 1
364 |  |  |  | float | 3 | 2 | 1
366 |  |  |  | float | 3 | 2 | 1
368 | Time Stamp(Demand Log 시작일) |  |  | U32 | 3 | 2 | 1
370 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
562 |  |  |  | float | 3 | 2 | 19
Voltage Quality RealTime Value
600 | Voltage Under Deviation L1 |  | % | float | 3 | 2 | 1
602 | Voltage Under Deviation L2 |  | % | float | 3 | 2 | 1
604 | Voltage Under Deviation L3 |  | % | float | 3 | 2 | 1
606 | Voltage Under Value L1 |  | rms | float | 3 | 2 | 1
608 | Voltage Under Value L2 |  | rms | float | 3 | 2 | 1
610 | Voltage Under Value L3 |  | rms | float | 3 | 2 | 1
612 | Voltage Over Deviation L1 |  | % | float | 3 | 2 | 1
614 | Voltage Over Deviation L2 |  | % | float | 3 | 2 | 1
616 | Voltage Over Deviation L3 |  | % | float | 3 | 2 | 1
618 | Voltage Over Value L1 |  | rms | float | 3 | 2 | 1
620 | Voltage Over Value L2 |  | rms | float | 3 | 2 | 1
622 | Voltage Over Value L3 |  | rms | float | 3 | 2 | 1
624 | Flickers Pi L1 | 150/180 Cycles |  | float | 3 | 2 | 1
626 | Flickers Pi L2 |  |  | float | 3 | 2 | 1
628 | Flickers Pi L3 |  |  | float | 3 | 2 | 1
630 | Flicker Pst L1 | 10min |  | float | 3 | 2 | 1
632 | Flicker Pst L2 |  |  | float | 3 | 2 | 1
634 | Flicker Pst L3 |  |  | float | 3 | 2 | 1
636 | Flicker Plt L1 | 2hr |  | float | 3 | 2 | 1 |  | 최근 24시간 그래프 그린다
638 | Flicker Plt L2 |  |  | float | 3 | 2 | 1
640 | Flicker Plt L3 |  |  | float | 3 | 2 | 1
642 | Signaling Volt L1 | Magnitude of current 10/12 cycles as a percentage of nominal voltage. |  | float | 3 | 2 | 1
644 | Signaling Volt L2 |  |  | float | 3 | 2 | 1
646 | Signaling Volt L3 |  |  | float | 3 | 2 | 1
648 | Signaling Volt Max L1 | Maximum magnitude of MSV from recording started as a percentage of nominal voltage |  | float | 3 | 2 | 1
650 | Signaling Volt Max L2 |  |  | float | 3 | 2 | 1
652 | Signaling Volt Max L3 |  |  | float | 3 | 2 | 1
654 |  |  |  | float | 3 | 2 | 23
EN50160 This Week
700 | start date |  |  | UTC | 3 | 2 | 1
702 | end date |  |  | UTC | 3 | 2 | 1
704 | status&compliance | bit 0: Freq Var1 bit 1: Freq Var2 bit 2: Volt Var1 L1 bit 3: Volt Var1 L2 bit 4: Volt Var1 L3 bit 5: Volt Var2 L1 bit 6: Volt Var2 L2 bit 7: Volt Var2 L3 bit 8: Unbalance bit 9: Volt THD L1 bit 10: Volt THD L2 bit 11: Volt THD L3 bit 12: Volt HD L1 bit 13: Volt HD L2 bit 14: Volt HD L3 bit 15: Pst L1 bit 16: Pst L2 bit 17: Pst L3 bit 18: Plt L1 bit 19: Plt L2 bit 20: Plt L3 bit 21: SigVolt L1 bit 22: SigVolt L2 bit 23: SigVolt L3 bit 31: Complete [status] 0: OK 1: failed |  | U32 | 3 | 2 | 1
706 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1 |  | 95%/Week
707 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1 |  | Info Only
708 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
709 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
710 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1 |  | 95%/Week
711 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
712 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
713 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1 |  | Info Only
714 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
715 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
716 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1 |  | Info Only
717 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
718 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
719 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1 |  | Info Only
720 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
721 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
722 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1 |  | Info Only
723 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
724 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
725 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1 |  | 95%/Week
726 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
727 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
728 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1 |  | 95%/Week
729 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
730 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
731 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1 |  | 99%/Day
732 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
733 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
734 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
735 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
736 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
737 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
738 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
739 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
740 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
741 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
742 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
743 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
744 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
745 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
746 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
747 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
748 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
749 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
EN50160 Last Week
750 | start date |  |  | UTC | 3 | 2 | 1
752 | end date |  |  | UTC | 3 | 2 | 1
754 | status |  |  | U16 | 3 | 1 | 1
755 | compilance |  |  | U16 | 3 | 1 | 1
756 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1
757 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1
758 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
759 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
760 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1
761 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
762 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
763 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1
764 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
765 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
766 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1
767 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
768 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
769 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1
770 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
771 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
772 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1
773 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
774 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
775 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1
776 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
777 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
778 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1
779 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
780 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
781 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1
782 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
783 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
784 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
785 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
786 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
787 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
788 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
789 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
790 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
791 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
792 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
793 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
794 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
795 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
796 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
797 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
798 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
799 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
Harmonics
800 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
864 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
928 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
992 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
1056 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
1120 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
1184 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
1248 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
1312 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
1376 |  |  |  | S16 | 3 | 1 | 24
Inter Harmonics
1400 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
1464 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
1528 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
1592 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
1656 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
1720 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
1784 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
1848 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
1912 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
1976 |  |  |  | S16 | 3 | 1 | 24
Max/Min
2000 | fr |  |  | U16 | 3 | 1 | 1
2001 | re |  |  | U16 | 3 | 1 | 1
2002 | Reset TimeStamp |  |  | UTC | 3 | 2 | 1
2004 | Frequency |  |  | float | 3 | 2 | 4
2012 | Temp |  |  | float | 3 | 2 | 4
2020 | U1 |  |  | float | 3 | 2 | 4
2028 | U2 |  |  | float | 3 | 2 | 4
2036 | U3 |  |  | float | 3 | 2 | 4 |  | http://www.relaytech.com/symcomp_calculator.htm
2044 | U~ |  |  | float | 3 | 2 | 4
2052 | U12 |  |  | float | 3 | 2 | 4
2060 | U23 |  |  | float | 3 | 2 | 4
2068 | U31 |  |  | float | 3 | 2 | 4
2076 | Upp~ |  |  | float | 3 | 2 | 4
2084 | I1 |  |  | float | 3 | 2 | 4
2092 | I2 |  |  | float | 3 | 2 | 4
2100 | I3 |  |  | float | 3 | 2 | 4
2108 | I~ |  |  | float | 3 | 2 | 4
2116 | I total |  |  | float | 3 | 2 | 4
2124 | In |  |  | float | 3 | 2 | 4
2132 | Isum |  |  | float | 3 | 2 | 4
2140 | P1 |  |  | float | 3 | 2 | 4
2148 | P2 |  |  | float | 3 | 2 | 4
2156 | P3 |  |  | float | 3 | 2 | 4
2164 | P total |  |  | float | 3 | 2 | 4
2172 | Q1 |  |  | float | 3 | 2 | 4
2180 | Q2 |  |  | float | 3 | 2 | 4
2188 | Q3 |  |  | float | 3 | 2 | 4
2196 | Q total |  |  | float | 3 | 2 | 4
2204 | S1 |  |  | float | 3 | 2 | 4
2212 | S2 |  |  | float | 3 | 2 | 4
2220 | S3 |  |  | float | 3 | 2 | 4
2228 | S total |  |  | float | 3 | 2 | 4
2236 | PF L1 |  |  | float | 3 | 2 | 4
2244 | PF L2 |  |  | float | 3 | 2 | 4
2252 | PF L3 |  |  | float | 3 | 2 | 4
2260 | PF total |  |  | float | 3 | 2 | 4
2268 | THD U1 |  |  | float | 3 | 2 | 4
2276 | THD U2 |  |  | float | 3 | 2 | 4
2284 | THD U3 |  |  | float | 3 | 2 | 4
2292 | THD U12 |  |  | float | 3 | 2 | 4
2300 | THD U23 |  |  | float | 3 | 2 | 4
2308 | THD U31 |  |  | float | 3 | 2 | 4
2316 | THD I1 |  |  | float | 3 | 2 | 4
2324 | THD I2 |  |  | float | 3 | 2 | 4
2332 | THD I3 |  |  | float | 3 | 2 | 4
2340 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
2342 | reserved |  |  | U16 | 3 | 1 | 1
2343 | CRC |  |  | U16 | 3 | 1 | 1
2344 |  |  |  | U16 | 3 | 1 | 6
alarm status
2350 | fr |  |  | U16 | 3 | 1 | 1
2351 | re |  |  | U16 | 3 | 1 | 1
2352 | reset Ts |  |  | UTC | 3 | 2 | 1
2354 | Alarm State #1 | Alarm Channel |  | U16 | 3 | 1 | 1
2355 |  | Alarm Condition |  | U16 | 3 | 1 | 1
2356 |  | Alarm Level |  | float | 3 | 2 | 1
2358 |  | Alarm Status |  | U16 | 3 | 1 | 1
2359 |  | Alarm Count |  | U16 | 3 | 1 | 1
2360 | Alarm State #2 |  |  | U16 | 3 | 1 | 6
2366 | Alarm State #3 |  |  | U16 | 3 | 1 | 6
2372 | Alarm State #4 |  |  | U16 | 3 | 1 | 6
2378 | Alarm State #5 |  |  | U16 | 3 | 1 | 6
2384 | Alarm State #6 |  |  | U16 | 3 | 1 | 6
2390 | Alarm State #7 |  |  | U16 | 3 | 1 | 6
2396 | Alarm State #8 |  |  | U16 | 3 | 1 | 6
2402 | Alarm State #9 |  |  | U16 | 3 | 1 | 6
2408 | Alarm State #10 |  |  | U16 | 3 | 1 | 6
2414 | Alarm State #11 |  |  | U16 | 3 | 1 | 6
2420 | Alarm State #12 |  |  | U16 | 3 | 1 | 6
2426 | Alarm State #13 |  |  | U16 | 3 | 1 | 6
2432 | Alarm State #14 |  |  | U16 | 3 | 1 | 6
2438 | Alarm State #15 |  |  | U16 | 3 | 1 | 6
2444 | Alarm State #16 |  |  | U16 | 3 | 1 | 6
2450 | Alarm State #17 |  |  | U16 | 3 | 1 | 6
2456 | Alarm State #18 |  |  | U16 | 3 | 1 | 6
2462 | Alarm State #19 |  |  | U16 | 3 | 1 | 6
2468 | Alarm State #20 |  |  | U16 | 3 | 1 | 6
2474 | Alarm State #21 |  |  | U16 | 3 | 1 | 6
2480 | Alarm State #22 |  |  | U16 | 3 | 1 | 6
2486 | Alarm State #23 |  |  | U16 | 3 | 1 | 6
2492 | Alarm State #24 |  |  | U16 | 3 | 1 | 6
2498 | Alarm State #25 |  |  | U16 | 3 | 1 | 6
2504 | Alarm State #26 |  |  | U16 | 3 | 1 | 6
2510 | Alarm State #27 |  |  | U16 | 3 | 1 | 6
2516 | Alarm State #28 |  |  | U16 | 3 | 1 | 6
2522 | Alarm State #29 |  |  | U16 | 3 | 1 | 6
2528 | Alarm State #30 |  |  | U16 | 3 | 1 | 6
2534 | Alarm State #31 |  |  | U16 | 3 | 1 | 6
2540 | Alarm State #32 |  |  | U16 | 3 | 1 | 6
2546 | update Ts |  |  | U32 | 3 | 2 | 1
2548 | Global Alarm Status | (alarm 하나라도 있으면 1, 아니면 0) |  | U16 | 3 | 1 | 1
2549 |  |  |  | U16 | 3 | 1 | 1
alarm log
2550 | fr | 0 ~ 1023 |  | U16 | 3 | 1 | 1
2551 | re | 0 ~ 1023 |  | U16 | 3 | 1 | 1
2552 | count | 전체 log 수 |  | U16 | 3 | 1 | 1
2553 | seq |  |  | U16 | 3 | 1 | 1
2554 | Alarm Log #1 | Time Stamp |  | UTC | 3 | 2 | 1 |  | 2019-5-11변경
2556 |  | status |  | U16 | 3 | 1 | 1
2557 |  | Alarm Channel & Condition |  | U16 | 3 | 1 | 1
2558 |  | level |  | float | 3 | 2 | 1
2560 |  | Value |  | float | 3 | 2 | 1
2562 | Alarm Log #2 |  |  | U16 | 3 | 1 | 8
2570 | Alarm Log #3 |  |  | U16 | 3 | 1 | 8
2578 | Alarm Log #4 |  |  | U16 | 3 | 1 | 8
2586 | Alarm Log #5 |  |  | U16 | 3 | 1 | 8
2594 | Alarm Log #6 |  |  | U16 | 3 | 1 | 8
2602 | Alarm Log #7 |  |  | U16 | 3 | 1 | 8
2610 | Alarm Log #8 |  |  | U16 | 3 | 1 | 8
2618 | Alarm Log #9 |  |  | U16 | 3 | 1 | 8
2626 | Alarm Log #10 |  |  | U16 | 3 | 1 | 8
2634 | Alarm Log #11 |  |  | U16 | 3 | 1 | 8
2642 | Alarm Log #12 |  |  | U16 | 3 | 1 | 8
2650 | Alarm Log #13 |  |  | U16 | 3 | 1 | 8
2658 | Alarm Log #14 |  |  | U16 | 3 | 1 | 8
2666 | Alarm Log #15 |  |  | U16 | 3 | 1 | 8
2674 | Alarm Log #16 |  |  | U16 | 3 | 1 | 8
2682 | Alarm Log #17 |  |  | U16 | 3 | 1 | 8
2690 | Alarm Log #18 |  |  | U16 | 3 | 1 | 8
2698 | Alarm Log #19 |  |  | U16 | 3 | 1 | 8
2706 | Alarm Log #20 |  |  | U16 | 3 | 1 | 8
2714 | Alarm Log #21 |  |  | U16 | 3 | 1 | 8
2722 | Alarm Log #22 |  |  | U16 | 3 | 1 | 8
2730 | Alarm Log #23 |  |  | U16 | 3 | 1 | 8
2738 | Alarm Log #24 |  |  | U16 | 3 | 1 | 8
2746 | Alarm Log #25 |  |  | U16 | 3 | 1 | 8
2754 | Alarm Log #26 |  |  | U16 | 3 | 1 | 8
2762 | Alarm Log #27 |  |  | U16 | 3 | 1 | 8
2770 | Alarm Log #28 |  |  | U16 | 3 | 1 | 8
2778 | Alarm Log #29 |  |  | U16 | 3 | 1 | 8
2786 | Alarm Log #30 |  |  | U16 | 3 | 1 | 8
2794 | Alarm Log #31 |  |  | U16 | 3 | 1 | 8
2802 | Alarm Log #32 |  |  | U16 | 3 | 1 | 8
2810 |  |  |  | U16 | 3 | 1 | 40
이벤트 리스트
2850 | fr | 0 ~ 1023 |  | U16 | 3 | 1 | 1
2851 | re | 0 ~ 1023 |  | U16 | 3 | 1 | 1
2852 | count | 0 ~ 1023 |  | U16 | 3 | 1 | 1
2853 | seq |  |  | U16 | 3 | 1 | 1
PQ 이벤트(Sag, Swell, Transient, OC)
2854 | start ts |  |  | UTC | 3 | 2 | 1
2856 | start ts(ms) |  |  | U16 | 3 | 1 | 1
2857 | duration |  |  | U16 | 3 | 1 | 1
2858 | type | 1 : E_SAG 2 : E_SWELL 3 : E_sINTR 4 : E_lINTR 5 : E_OC 6 : E_RVC 7 : E_TrV 8 : E_TrC |  | U16 | 3 | 1 | 1
2859 | mask |  |  | U16 | 3 | 1 | 1
2860 | Level 1 |  |  | float | 3 | 2 | 1
2862 | Level 2 |  |  | float | 3 | 2 | 1
2864 | Level 3 |  |  | float | 3 | 2 | 1
2866 | PQ Event #2 |  |  | U16 | 3 | 1 | 12
2878 | PQ Event #3 |  |  | U16 | 3 | 1 | 12
2890 | PQ Event #4 |  |  | U16 | 3 | 1 | 12
2902 | PQ Event #5 |  |  | U16 | 3 | 1 | 12
2914 | PQ Event #6 |  |  | U16 | 3 | 1 | 12
2926 | PQ Event #7 |  |  | U16 | 3 | 1 | 12
2938 | PQ Event #8 |  |  | U16 | 3 | 1 | 12
2950 | PQ Event #9 |  |  | U16 | 3 | 1 | 12
2962 | PQ Event #10 |  |  | U16 | 3 | 1 | 12
2974 | PQ Event #11 |  |  | U16 | 3 | 1 | 12
2986 | PQ Event #12 |  |  | U16 | 3 | 1 | 12
2998 | PQ Event #13 |  |  | U16 | 3 | 1 | 12
3010 | PQ Event #14 |  |  | U16 | 3 | 1 | 12
3022 | PQ Event #15 |  |  | U16 | 3 | 1 | 12
3034 | PQ Event #16 |  |  | U16 | 3 | 1 | 12
3046 | PQ Event #17 |  |  | U16 | 3 | 1 | 12
3058 | PQ Event #18 |  |  | U16 | 3 | 1 | 12
3070 | PQ Event #19 |  |  | U16 | 3 | 1 | 12
3082 | PQ Event #20 |  |  | U16 | 3 | 1 | 12
3094 | PQ Event #21 |  |  | U16 | 3 | 1 | 12
3106 | PQ Event #22 |  |  | U16 | 3 | 1 | 12
3118 | PQ Event #23 |  |  | U16 | 3 | 1 | 12
3130 | PQ Event #24 |  |  | U16 | 3 | 1 | 12
3142 | PQ Event #25 |  |  | U16 | 3 | 1 | 12
3154 | PQ Event #26 |  |  | U16 | 3 | 1 | 12
3166 | PQ Event #27 |  |  | U16 | 3 | 1 | 12
3178 | PQ Event #28 |  |  | U16 | 3 | 1 | 12
3190 | PQ Event #29 |  |  | U16 | 3 | 1 | 12
3202 | PQ Event #30 |  |  | U16 | 3 | 1 | 12
3214 | PQ Event #31 |  |  | U16 | 3 | 1 | 12
3226 | PQ Event #32 |  |  | U16 | 3 | 1 | 12
3238 |  |  |  | U16 | 3 | 1 | 2
PQ Event Counter
3240 |  |  |  | U16 | 3 | 1 | 1
3241 |  |  |  | U16 | 3 | 1 | 1
3242 |  |  |  | U16 | 3 | 1 | 1
3243 | Sag Coount |  |  | U16 | 3 | 1 | 1
3244 | Swell Count |  |  | U16 | 3 | 1 | 1
3245 |  |  |  | U16 | 3 | 1 | 1
3246 |  |  |  | U16 | 3 | 1 | 1
3247 |  |  |  | U16 | 3 | 1 | 1
3248 |  |  |  | U16 | 3 | 1 | 1
3249 |  |  |  | U16 | 3 | 1 | 1
Wave Sample | [8 empty] | 32K: 67,107,786 8K: 74,518,668 첫번째 번지 접근시 wave data를 modbus map으로 load 한다
3250 | Wave Form V1 (160 sample) |  |  | S16 | 3 | 1 | 160
3410 | Wave Form V2 (160 sample) |  |  | S16 | 3 | 1 | 160
3570 | Wave Form V3 (160 sample) |  |  | S16 | 3 | 1 | 160
3730 | Wave Form V12 (160 sample) |  |  | S16 | 3 | 1 | 160
3890 | Wave Form V23 (160 sample) |  |  | S16 | 3 | 1 | 160
4050 | Wave Form V31 (160 sample) |  |  | S16 | 3 | 1 | 160
4210 | Wave Form I1 (160 sample) |  |  | S16 | 3 | 1 | 160
4370 | Wave Form I2 (160 sample) |  |  | S16 | 3 | 1 | 160
4530 | Wave Form I3 (160 sample) |  |  | S16 | 3 | 1 | 160
4690 | vscale |  |  | float | 3 | 2 | 1
4692 | iscale |  |  | float | 3 | 2 | 1
4694 |  |  |  | S16 | 3 | 1 | 6
월간리포트 생성위한 10분 평균
4700 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
4702 | U1 |  |  | float | 3 | 2 | 1
4704 | U2 |  |  | float | 3 | 2 | 1
4706 | U3 |  |  | float | 3 | 2 | 1
4708 | U THD1 |  |  | float | 3 | 2 | 1
4710 | U THD2 |  |  | float | 3 | 2 | 1
4712 | U THD3 |  |  | float | 3 | 2 | 1
4714 | Upp THD1 |  |  | float | 3 | 2 | 1
4716 | Upp THD2 |  |  | float | 3 | 2 | 1
4718 | Upp THD3 |  |  | float | 3 | 2 | 1
4720 | U Unbal Uu |  |  | float | 3 | 2 | 1
4722 | U Unbal Uo |  |  | float | 3 | 2 | 1
4724 | I1 |  |  | float | 3 | 2 | 1
4726 | I2 |  |  | float | 3 | 2 | 1
4728 | I3 |  |  | float | 3 | 2 | 1
4730 | In |  |  | float | 3 | 2 | 1
4732 | I THD1 |  |  | float | 3 | 2 | 1
4734 | I THD2 |  |  | float | 3 | 2 | 1
4736 | I THD3 |  |  | float | 3 | 2 | 1
4738 | I TDD1 |  |  | float | 3 | 2 | 1
4740 | I TDD2 |  |  | float | 3 | 2 | 1
4742 | I TDD3 |  |  | float | 3 | 2 | 1
4744 | K-factor 1 |  |  | float | 3 | 2 | 1
4746 | K-factor 2 |  |  | float | 3 | 2 | 1
4748 | K-factor 3 |  |  | float | 3 | 2 | 1
4750 | I Unbal Iu |  |  | float | 3 | 2 | 1
4752 | I Unbal Io |  |  | float | 3 | 2 | 1
4754 | kw imp |  |  | float | 3 | 2 | 1
4756 | kw exp |  |  | float | 3 | 2 | 1
4758 | kvar lag |  |  | float | 3 | 2 | 1
4760 | kvar lead |  |  | float | 3 | 2 | 1
4762 | kVA |  |  | float | 3 | 2 | 1
4764 | PF |  |  | float | 3 | 2 | 1
4766 | dPF |  |  | float | 3 | 2 | 1
4768 | temperature #1 |  |  | float | 3 | 2 | 1
4770 | temperature #2 |  |  | float | 3 | 2 | 1
4772 | temperature #3 |  |  | float | 3 | 2 | 1
4774 | temperature #4 |  |  | float | 3 | 2 | 1
4776 | temperature #5 |  |  | float | 3 | 2 | 1 |  | *통신이 끊어진 경우 복구를 위해 사용된다
4778 | Harmonics V1 |  |  | S16 | 3 | 1 | 24
4802 | Harmonics V2 |  |  | S16 | 3 | 1 | 24 |  | demand
4826 | Harmonics V3 |  |  | S16 | 3 | 1 | 24
4850 | Harmonics V12 |  |  | S16 | 3 | 1 | 24
4874 | Harmonics V23 |  |  | S16 | 3 | 1 | 24
4898 | Harmonics V31 |  |  | S16 | 3 | 1 | 24
4922 | Harmonics I1 |  |  | S16 | 3 | 1 | 24
4946 | Harmonics I2 |  |  | S16 | 3 | 1 | 24
4970 | Harmonics I3 |  |  | S16 | 3 | 1 | 24
4994 |  |  |  | U16 | 3 | 1 | 6
Energy log
5000 | Time Stamp |  |  | UTC | 3 | 2 | 1
5002 | kwh import |  |  | float | 3 | 2 | 1
5004 | kvarh lag |  |  | float | 3 | 2 | 1
5006 | kvarh lead |  |  | float | 3 | 2 | 1
5008 | kVAh |  |  | float | 3 | 2 | 1
5010 | energy log last day 01h |  |  | float | 3 | 2 | 4
5018 | energy log last day 02h |  |  | float | 3 | 2 | 4
5026 | energy log last day 03h |  |  | float | 3 | 2 | 4
5034 | energy log last day 04h |  |  | float | 3 | 2 | 4
5042 | energy log last day 05h |  |  | float | 3 | 2 | 4
5050 | energy log last day 06h |  |  | float | 3 | 2 | 4
5058 | energy log last day 07h |  |  | float | 3 | 2 | 4
5066 | energy log last day 08h |  |  | float | 3 | 2 | 4
5074 | energy log last day 09h |  |  | float | 3 | 2 | 4
5082 | energy log last day 10h |  |  | float | 3 | 2 | 4
5090 | energy log last day 11h |  |  | float | 3 | 2 | 4
5098 | energy log last day 12h |  |  | float | 3 | 2 | 4
5106 | energy log last day 13h |  |  | float | 3 | 2 | 4
5114 | energy log last day 14h |  |  | float | 3 | 2 | 4
5122 | energy log last day 15h |  |  | float | 3 | 2 | 4
5130 | energy log last day 16h |  |  | float | 3 | 2 | 4
5138 | energy log last day 17h |  |  | float | 3 | 2 | 4
5146 | energy log last day 18h |  |  | float | 3 | 2 | 4
5154 | energy log last day 19h |  |  | float | 3 | 2 | 4
5162 | energy log last day 20h |  |  | float | 3 | 2 | 4
5170 | energy log last day 21h |  |  | float | 3 | 2 | 4
5178 | energy log last day 22h |  |  | float | 3 | 2 | 4
5186 | energy log last day 23h |  |  | float | 3 | 2 | 4
5194 |  |  |  | U16 | 3 | 1 | 6
5200 | Time Stamp |  |  | UTC | 3 | 2 | 1
5202 | kwh import |  |  | float | 3 | 2 | 1
5204 | kvarh lag |  |  | float | 3 | 2 | 1
5206 | kvarh lead |  |  | float | 3 | 2 | 1
5208 | kVAh |  |  | float | 3 | 2 | 1
5210 | energy log this day 01h |  |  | float | 3 | 2 | 4
5218 | energy log this day 02h |  |  | float | 3 | 2 | 4
5226 | energy log this day 03h |  |  | float | 3 | 2 | 4
5234 | energy log this day 04h |  |  | float | 3 | 2 | 4
5242 | energy log this day 05h |  |  | float | 3 | 2 | 4
5250 | energy log this day 06h |  |  | float | 3 | 2 | 4
5258 | energy log this day 07h |  |  | float | 3 | 2 | 4
5266 | energy log this day 08h |  |  | float | 3 | 2 | 4
5274 | energy log this day 09h |  |  | float | 3 | 2 | 4
5282 | energy log this day 10h |  |  | float | 3 | 2 | 4
5290 | energy log this day 11h |  |  | float | 3 | 2 | 4
5298 | energy log this day 12h |  |  | float | 3 | 2 | 4
5306 | energy log this day 13h |  |  | float | 3 | 2 | 4
5314 | energy log this day 14h |  |  | float | 3 | 2 | 4 |  | 전일 디멘트 로그
5322 | energy log this day 15h |  |  | float | 3 | 2 | 4
5330 | energy log this day 16h |  |  | float | 3 | 2 | 4
5338 | energy log this day 17h |  |  | float | 3 | 2 | 4
5346 | energy log this day 18h |  |  | float | 3 | 2 | 4
5354 | energy log this day 19h |  |  | float | 3 | 2 | 4
5362 | energy log this day 20h |  |  | float | 3 | 2 | 4
5370 | energy log this day 21h |  |  | float | 3 | 2 | 4
5378 | energy log this day 22h |  |  | float | 3 | 2 | 4
5386 | energy log this day 23h |  |  | float | 3 | 2 | 4
5394 |  |  |  | U16 | 3 | 1 | 6
demand log last day
5400 | Time Stamp |  |  | U32 | 3 | 2 | 1
5402 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
5594 |  |  |  | U16 | 3 | 1 | 6
Max/Min last data
5600 | fr |  |  | S16 | 3 | 1 | 1
5601 | re |  |  | S16 | 3 | 1 | 1
5602 | Reset TimeStamp |  |  | UTC | 3 | 2 | 1
5604 | Frequency |  |  | float | 3 | 2 | 4
5612 | Temp |  |  | float | 3 | 2 | 4
5620 | U1 |  |  | float | 3 | 2 | 4
5628 | U2 |  |  | float | 3 | 2 | 4
5636 | U3 |  |  | float | 3 | 2 | 4
5644 | U~ |  |  | float | 3 | 2 | 4
5652 | U12 |  |  | float | 3 | 2 | 4
5660 | U23 |  |  | float | 3 | 2 | 4
5668 | U31 |  |  | float | 3 | 2 | 4
5676 | Upp~ |  |  | float | 3 | 2 | 4
5684 | I1 |  |  | float | 3 | 2 | 4
5692 | I2 |  |  | float | 3 | 2 | 4
5700 | I3 |  |  | float | 3 | 2 | 4
5708 | I~ |  |  | float | 3 | 2 | 4
5716 | I total |  |  | float | 3 | 2 | 4
5724 | In |  |  | float | 3 | 2 | 4
5732 | Isum |  |  | float | 3 | 2 | 4
5740 | P1 |  |  | float | 3 | 2 | 4
5748 | P2 |  |  | float | 3 | 2 | 4
5756 | P3 |  |  | float | 3 | 2 | 4
5764 | P total |  |  | float | 3 | 2 | 4
5772 | Q1 |  |  | float | 3 | 2 | 4
5780 | Q2 |  |  | float | 3 | 2 | 4
5788 | Q3 |  |  | float | 3 | 2 | 4
5796 | Q total |  |  | float | 3 | 2 | 4
5804 | S1 |  |  | float | 3 | 2 | 4
5812 | S2 |  |  | float | 3 | 2 | 4
5820 | S3 |  |  | float | 3 | 2 | 4
5828 | S total |  |  | float | 3 | 2 | 4
5836 | PF L1 |  |  | float | 3 | 2 | 4
5844 | PF L2 |  |  | float | 3 | 2 | 4
5852 | PF L3 |  |  | float | 3 | 2 | 4
5860 | PF total |  |  | float | 3 | 2 | 4
5868 | THD U1 |  |  | float | 3 | 2 | 4
5876 | THD U2 |  |  | float | 3 | 2 | 4
5884 | THD U3 |  |  | float | 3 | 2 | 4
5892 | THD U12 |  |  | float | 3 | 2 | 4
5900 | THD U23 |  |  | float | 3 | 2 | 4
5908 | THD U31 |  |  | float | 3 | 2 | 4
5916 | THD I1 |  |  | float | 3 | 2 | 4
5924 | THD I2 |  |  | float | 3 | 2 | 4
5932 | THD I3 |  |  | float | 3 | 2 | 4
5940 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
5942 | reserved |  |  | U16 | 3 | 1 | 1
5943 | CRC |  |  | U16 | 3 | 1 | 1
5944 |  |  |  | U16 | 3 | 1 | 6
ITIC
5950 | fr |  |  | U16 | 3 | 1 | 1
5951 | re |  |  | U16 | 3 | 1 | 1
5952 | count |  |  | U16 | 3 | 1 | 1
5953 | SEQ |  |  | U16 | 3 | 1 | 1
5954 | Log #1 | start ts |  | UTC | 3 | 2 | 1
5956 |  | start ts(ms) |  | U16 | 3 | 1 | 1
5957 |  | duration |  | U16 | 3 | 1 | 1
5958 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
5959 |  | mask |  | U16 | 3 | 1 | 1
5960 |  | Level 1 |  | float | 3 | 2 | 1
5962 |  | Level 2 |  | float | 3 | 2 | 1
5964 |  | Level 3 |  | float | 3 | 2 | 1
5966 |  | Normal |  | float | 3 | 2 | 1
5968 | Log #2 |  |  | U16 | 3 | 1 | 14
5982 | Log #3 |  |  | U16 | 3 | 1 | 14
5996 | Log #4 |  |  | U16 | 3 | 1 | 14
6010 | Log #5 |  |  | U16 | 3 | 1 | 14
6024 | Log #6 |  |  | U16 | 3 | 1 | 14
6038 | Log #7 |  |  | U16 | 3 | 1 | 14
6052 | Log #8 |  |  | U16 | 3 | 1 | 14
6066 | Log #9 |  |  | U16 | 3 | 1 | 14
6080 | Log #10 |  |  | U16 | 3 | 1 | 14
6094 | Log #11 |  |  | U16 | 3 | 1 | 14
6108 | Log #12 |  |  | U16 | 3 | 1 | 14
6122 | Log #13 |  |  | U16 | 3 | 1 | 14
6136 | Log #14 |  |  | U16 | 3 | 1 | 14
6150 | Log #15 |  |  | U16 | 3 | 1 | 14
6164 | Log #16 |  |  | U16 | 3 | 1 | 14
6178 | Log #17 |  |  | U16 | 3 | 1 | 14
6192 | Log #18 |  |  | U16 | 3 | 1 | 14
6206 | Log #19 |  |  | U16 | 3 | 1 | 14
6220 | Log #20 |  |  | U16 | 3 | 1 | 14
6234 | Log #21 |  |  | U16 | 3 | 1 | 14
6248 | Log #22 |  |  | U16 | 3 | 1 | 14
6262 | Log #23 |  |  | U16 | 3 | 1 | 14
6276 | Log #24 |  |  | U16 | 3 | 1 | 14
6290 | Log #25 |  |  | U16 | 3 | 1 | 14
6304 | Log #26 |  |  | U16 | 3 | 1 | 14
6318 | Log #27 |  |  | U16 | 3 | 1 | 14
6332 | Log #28 |  |  | U16 | 3 | 1 | 14
6346 | Log #29 |  |  | U16 | 3 | 1 | 14
6360 | Log #30 |  |  | U16 | 3 | 1 | 14
6374 | Log #31 |  |  | U16 | 3 | 1 | 14
6388 | Log #32 |  |  | U16 | 3 | 1 | 14
6402 |  |  |  | U16 | 3 | 1 | 8
ITIC(Configurator)
6410 | fr |  |  | U16 | 3 | 1 | 1
6411 | re |  |  | U16 | 3 | 1 | 1
6412 | count |  |  | U16 | 3 | 1 | 1
6413 | reserved |  |  | U16 | 3 | 1 | 1
6414 | Log #1 | start ts |  | UTC | 3 | 2 | 1
6416 |  | start ts(ms) |  | U16 | 3 | 1 | 1
6417 |  | duration |  | U16 | 3 | 1 | 1
6418 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
6419 |  | mask |  | U16 | 3 | 1 | 1
6420 |  | Level 1 |  | float | 3 | 2 | 1
6422 |  | Level 2 |  | float | 3 | 2 | 1
6424 |  | Level 3 |  | float | 3 | 2 | 1
6426 |  | Normal |  | float | 3 | 2 | 1
6428 | Log #2 |  |  | U16 | 3 | 1 | 14
6442 | Log #3 |  |  | U16 | 3 | 1 | 14
6456 | Log #4 |  |  | U16 | 3 | 1 | 14
6470 | Log #5 |  |  | U16 | 3 | 1 | 14
6484 | Log #6 |  |  | U16 | 3 | 1 | 14
6498 | Log #7 |  |  | U16 | 3 | 1 | 14
6512 | Log #8 |  |  | U16 | 3 | 1 | 14
6526 | Log #9 |  |  | U16 | 3 | 1 | 14
6540 | Log #10 |  |  | U16 | 3 | 1 | 14
6554 | Log #11 |  |  | U16 | 3 | 1 | 14
6568 | Log #12 |  |  | U16 | 3 | 1 | 14
6582 | Log #13 |  |  | U16 | 3 | 1 | 14
6596 | Log #14 |  |  | U16 | 3 | 1 | 14
6610 | Log #15 |  |  | U16 | 3 | 1 | 14
6624 | Log #16 |  |  | U16 | 3 | 1 | 14
6638 | Log #17 |  |  | U16 | 3 | 1 | 14
6652 | Log #18 |  |  | U16 | 3 | 1 | 14
6666 | Log #19 |  |  | U16 | 3 | 1 | 14
6680 | Log #20 |  |  | U16 | 3 | 1 | 14
6694 | Log #21 |  |  | U16 | 3 | 1 | 14
6708 | Log #22 |  |  | U16 | 3 | 1 | 14
6722 | Log #23 |  |  | U16 | 3 | 1 | 14
6736 | Log #24 |  |  | U16 | 3 | 1 | 14
6750 | Log #25 |  |  | U16 | 3 | 1 | 14
6764 | Log #26 |  |  | U16 | 3 | 1 | 14
6778 | Log #27 |  |  | U16 | 3 | 1 | 14
6792 | Log #28 |  |  | U16 | 3 | 1 | 14
6806 | Log #29 |  |  | U16 | 3 | 1 | 14
6820 | Log #30 |  |  | U16 | 3 | 1 | 14
6834 | Log #31 |  |  | U16 | 3 | 1 | 14
6848 | Log #32 |  |  | U16 | 3 | 1 | 14
6862 |  |  |  | U16 | 3 | 1 | 8
IOM Data
6870 | DI status #0 |  |  | U16 | 3 | 1 | 1
6871 | DI status #1 |  |  | U16 | 3 | 1 | 1
6872 | DI status #2 |  |  | U16 | 3 | 1 | 1
6873 | DI status #3 |  |  | U16 | 3 | 1 | 1
6874 | DI Pulse Data #0 |  |  | U32 | 3 | 2 | 1
6876 | DI Pulse Data #1 |  |  | U32 | 3 | 2 | 1
6878 | DI Pulse Data #2 |  |  | U32 | 3 | 2 | 1
6880 | DI Pulse Data #3 |  |  | U32 | 3 | 2 | 1
6882 | TEMP #0 |  |  | float | 3 | 2 | 1
6884 | TEMP #1 |  |  | float | 3 | 2 | 1
6886 | TEMP #2 |  |  | float | 3 | 2 | 1
6888 | TEMP #3 |  |  | float | 3 | 2 | 1
METER INFO
6890 | serial# |  |  | U16 | 3 | 1 | 6
6896 | MAC MSB |  |  | U16 | 3 | 1 | 2
6898 | mac address |  |  | U16 | 3 | 1 | 4
6902 | IP ADDR |  |  | U16 | 3 | 1 | 4
6906 | HW Model |  |  | U16 | 3 | 1 | 1
6907 | HW version |  |  | U16 | 3 | 1 | 1
6908 | FW version |  |  | U16 | 3 | 1 | 1
6909 | FW_BUILD_YEAR |  |  | U16 | 3 | 1 | 1
6910 | FW_BUILD_MON |  |  | U16 | 3 | 1 | 1
6911 | FW_BUILD_DAY |  |  | U16 | 3 | 1 | 1
6912 | HEART BIT |  |  | U16 | 3 | 1 | 1
6913 | MODBUS RX COUNT |  |  | U16 | 3 | 1 | 1
6914 | ALARM STS |  |  | U16 | 3 | 1 | 1
6915 | EVENT STS |  |  | U16 | 3 | 1 | 1
6916 | RSTP STS[0~1] |  |  | U16 | 3 | 1 | 2
6918 | SNTP STS |  |  | U16 | 3 | 1 | 1
6919 | DEV STS |  |  | U16 | 3 | 1 | 1
6920 | NET STS |  |  | U16 | 3 | 1 | 1
6921 | TOT STS |  |  | U16 | 3 | 1 | 1
6912 | reserved |  |  | U16 | 3 | 1 | 8
Setting 영역 시작
PQ Event
6920 | OC Level | 정격의 2배 |  | U16 | 3,16 | 1 | 1
6921 | OC Cycle | unused |  | U16 | 3,16 | 1 | 1
6922 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
6923 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
6924 |  |  |  | U16 | 3,16 | 1 | 2
6926 | Sag Level(%), 90% | < 90% |  | U16 | 3,16 | 1 | 1
6927 | Sag Cycle | unused |  | U16 | 3,16 | 1 | 1
6928 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
6929 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
6930 |  |  |  | U16 | 3,16 | 1 | 2
6932 | Swell Level(%), 110~200~ | > 110% |  | U16 | 3,16 | 1 | 1
6933 | Swell Cycle | unused |  | U16 | 3,16 | 1 | 1
6934 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
6935 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
6936 |  |  |  | U16 | 3,16 | 1 | 2
6938 | Interruption Level, 5% | < 5% |  | U16 | 3,16 | 1 | 1
6939 | Interruption Time, 60s | unused |  | U16 | 3,16 | 1 | 1
6940 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
6941 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
6942 |  |  |  | U16 | 3,16 | 1 | 2
Transient Trigger
6944 | Transient Voltage, HoldOff Time, 20ms | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
6945 | Transient Voltage, Absolute Peak Level, 200% | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
6946 | Transient Voltage, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
6947 | Transient Voltage, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
6948 | Transient Current, HoldOff Time | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
6949 | Transient Current, Absolute Peak Level | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
6950 | Transient Current, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
6951 | Transient Current, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
6952 |  |  |  | U16 | 3,16 | 1 | 12
Recorder
Waveform
6964 | Recorder resolution(32k, 8k) |  |  | U16 | 3,16 | 1 | 1
6965 | Recorded paramater (U or I) |  |  | U16 | 3,16 | 1 | 1
6966 | pre trigger time(0.1s) |  |  | U16 | 3,16 | 1 | 1
6967 | post trigger time(1s) |  |  | U16 | 3,16 | 1 | 1
Disturbance
6968 | Recorder resolution (Half Cycle) |  |  | U16 | 3,16 | 1 | 1
6969 | Recorded parametrs(U or I) |  |  | U16 | 3,16 | 1 | 1
6970 | pre trigger time(100 sample) |  |  | U16 | 3,16 | 1 | 1
6971 | post trigger time(900 sample) |  |  | U16 | 3,16 | 1 | 1
6972 |  |  |  | U16 | 3,16 | 1 | 12
Trend Recorder
6984 | Trend Group #1 Active |  |  | U16 | 3,16 | 1 | 1
6985 | Trend Group #1 Storage Interval |  |  | U16 | 3,16 | 1 | 1
6986 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
6987 | Trend Group #1, Channel #1 |  |  | U16 | 3,16 | 1 | 1
6988 | Trend Group #1, Channel #2 |  |  | U16 | 3,16 | 1 | 1
6989 | Trend Group #1, Channel #3 |  |  | U16 | 3,16 | 1 | 1
6990 | Trend Group #1, Channel #4 |  |  | U16 | 3,16 | 1 | 1
6991 | Trend Group #1, Channel #5 |  |  | U16 | 3,16 | 1 | 1
6992 | Trend Group #1, Channel #6 |  |  | U16 | 3,16 | 1 | 1
6993 | Trend Group #1, Channel #7 |  |  | U16 | 3,16 | 1 | 1
6994 | Trend Group #1, Channel #8 |  |  | U16 | 3,16 | 1 | 1
6995 | Trend Group #1, Channel #9 |  |  | U16 | 3,16 | 1 | 1
6996 | Trend Group #1, Channel #10 |  |  | U16 | 3,16 | 1 | 1
6997 | Trend Group #1, Channel #11 |  |  | U16 | 3,16 | 1 | 1
6998 | Trend Group #1, Channel #12 |  |  | U16 | 3,16 | 1 | 1
6999 | Trend Group #1, Channel #13 |  |  | U16 | 3,16 | 1 | 1
7000 | Trend Group #1, Channel #14 |  |  | U16 | 3,16 | 1 | 1
7001 | Trend Group #1, Channel #15 |  |  | U16 | 3,16 | 1 | 1
7002 | Trend Group #1, Channel #16 |  |  | U16 | 3,16 | 1 | 1
7003 | Trend Group #2 Active |  |  | U16 | 3,16 | 1 | 1
7004 | Trend Group #2 Storage Interval |  |  | U16 | 3,16 | 1 | 1
7005 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
7006 | Trend Group #2, Channel #1 |  |  | U16 | 3,16 | 1 | 1
7007 | Trend Group #2, Channel #2 |  |  | U16 | 3,16 | 1 | 1
7008 | Trend Group #2, Channel #3 |  |  | U16 | 3,16 | 1 | 1
7009 | Trend Group #2, Channel #4 |  |  | U16 | 3,16 | 1 | 1
7010 | Trend Group #2, Channel #5 |  |  | U16 | 3,16 | 1 | 1
7011 | Trend Group #2, Channel #6 |  |  | U16 | 3,16 | 1 | 1
7012 | Trend Group #2, Channel #7 |  |  | U16 | 3,16 | 1 | 1
7013 | Trend Group #2, Channel #8 |  |  | U16 | 3,16 | 1 | 1
7014 | Trend Group #2, Channel #9 |  |  | U16 | 3,16 | 1 | 1
7015 | Trend Group #2, Channel #10 |  |  | U16 | 3,16 | 1 | 1
7016 | Trend Group #2, Channel #11 |  |  | U16 | 3,16 | 1 | 1
7017 | Trend Group #2, Channel #12 |  |  | U16 | 3,16 | 1 | 1
7018 | Trend Group #2, Channel #13 |  |  | U16 | 3,16 | 1 | 1
7019 | Trend Group #2, Channel #14 |  |  | U16 | 3,16 | 1 | 1
7020 | Trend Group #2, Channel #15 |  |  | U16 | 3,16 | 1 | 1
7021 | Trend Group #2, Channel #16 |  |  | U16 | 3,16 | 1 | 1
7022 | Trend Group #3 Active |  |  | U16 | 3,16 | 1 | 1
7023 | Trend Group #3 Storage Interval |  |  | U16 | 3,16 | 1 | 1
7024 |  |  |  | U16 | 3,16 | 1 | 1
7025 | Trend Group #3, Channel #1 |  |  | U16 | 3,16 | 1 | 1
7026 | Trend Group #3, Channel #2 |  |  | U16 | 3,16 | 1 | 1
7027 | Trend Group #3, Channel #3 |  |  | U16 | 3,16 | 1 | 1
7028 | Trend Group #3, Channel #4 |  |  | U16 | 3,16 | 1 | 1
7029 | Trend Group #3, Channel #5 |  |  | U16 | 3,16 | 1 | 1
7030 | Trend Group #3, Channel #6 |  |  | U16 | 3,16 | 1 | 1
7031 | Trend Group #3, Channel #7 |  |  | U16 | 3,16 | 1 | 1
7032 | Trend Group #3, Channel #8 |  |  | U16 | 3,16 | 1 | 1
7033 | Trend Group #3, Channel #9 |  |  | U16 | 3,16 | 1 | 1
7034 | Trend Group #3, Channel #10 |  |  | U16 | 3,16 | 1 | 1
7035 | Trend Group #3, Channel #11 |  |  | U16 | 3,16 | 1 | 1
7036 | Trend Group #3, Channel #12 |  |  | U16 | 3,16 | 1 | 1
7037 | Trend Group #3, Channel #13 |  |  | U16 | 3,16 | 1 | 1
7038 | Trend Group #3, Channel #14 |  |  | U16 | 3,16 | 1 | 1
7039 | Trend Group #3, Channel #15 |  |  | U16 | 3,16 | 1 | 1
7040 | Trend Group #3, Channel #16 |  |  | U16 | 3,16 | 1 | 1
7041 | Trend Group #4 Active |  |  | U16 | 3,16 | 1 | 1
7042 | Trend Group #4 Storage Interval |  |  | U16 | 3,16 | 1 | 1
7043 |  |  |  | U16 | 3,16 | 1 | 1
7044 | Trend Group #4, Channel #1 |  |  | U16 | 3,16 | 1 | 1
7045 | Trend Group #4, Channel #2 |  |  | U16 | 3,16 | 1 | 1
7046 | Trend Group #4, Channel #3 |  |  | U16 | 3,16 | 1 | 1
7047 | Trend Group #4, Channel #4 |  |  | U16 | 3,16 | 1 | 1
7048 | Trend Group #4, Channel #5 |  |  | U16 | 3,16 | 1 | 1
7049 | Trend Group #4, Channel #6 |  |  | U16 | 3,16 | 1 | 1
7050 | Trend Group #4, Channel #7 |  |  | U16 | 3,16 | 1 | 1
7051 | Trend Group #4, Channel #8 |  |  | U16 | 3,16 | 1 | 1
7052 | Trend Group #4, Channel #9 |  |  | U16 | 3,16 | 1 | 1
7053 | Trend Group #4, Channel #10 |  |  | U16 | 3,16 | 1 | 1
7054 | Trend Group #4, Channel #11 |  |  | U16 | 3,16 | 1 | 1
7055 | Trend Group #4, Channel #12 |  |  | U16 | 3,16 | 1 | 1
7056 | Trend Group #4, Channel #13 |  |  | U16 | 3,16 | 1 | 1
7057 | Trend Group #4, Channel #14 |  |  | U16 | 3,16 | 1 | 1
7058 | Trend Group #4, Channel #15 |  |  | U16 | 3,16 | 1 | 1
7059 | Trend Group #4, Channel #16 |  |  | U16 | 3,16 | 1 | 1
7060 |  |  |  | U16 | 3,16 | 1 | 4
Power Quality Report
7064 | Active |  |  | U16 | 3,16 | 1 | 1
7065 | Start Day |  |  | U16 | 3,16 | 1 | 1
7066 |  |  |  | U16 |  | 1 | 8
Alarm Definition
7074 | compare Time Delay(1s) |  |  | U16 | 3,16 | 1 | 1
7075 |  |  |  | U16 |  | 1 | 1
7076 |  |  |  | U16 |  | 1 | 1
7077 |  |  |  | U16 |  | 1 | 1
Alarm Settings
7078 | Alarm Info #1 Channel(0:disabled, >0: enabled) |  |  | U16 | 3,16 | 1 | 1
7079 | Alarm Cond (0: < , 1:>) |  |  | U16 | 3,16 | 1 | 1
7080 | Hysteresis (% of Nominal) |  |  | U16 | 3,16 | 1 | 1
7081 | Alarm Action (None, Relay or Beep) |  |  | U16 | 3,16 | 1 | 1
7082 | Alarm Level |  |  | float | 3,16 | 2 | 1
7084 | Alarm Settings #2 |  |  | U16 | 3,16 | 1 | 6
7090 | Alarm Settings #3 |  |  | U16 | 3,16 | 1 | 6
7096 | Alarm Settings #4 |  |  | U16 | 3,16 | 1 | 6
7102 | Alarm Settings #5 |  |  | U16 | 3,16 | 1 | 6
7108 | Alarm Settings #6 |  |  | U16 | 3,16 | 1 | 6
7114 | Alarm Settings #7 |  |  | U16 | 3,16 | 1 | 6
7120 | Alarm Settings #8 |  |  | U16 | 3,16 | 1 | 6
7126 | Alarm Settings #9 |  |  | U16 | 3,16 | 1 | 6
7132 | Alarm Settings #10 |  |  | U16 | 3,16 | 1 | 6
7138 | Alarm Settings #11 |  |  | U16 | 3,16 | 1 | 6
7144 | Alarm Settings #12 |  |  | U16 | 3,16 | 1 | 6
7150 | Alarm Settings #13 |  |  | U16 | 3,16 | 1 | 6
7156 | Alarm Settings #14 |  |  | U16 | 3,16 | 1 | 6
7162 | Alarm Settings #15 |  |  | U16 | 3,16 | 1 | 6
7168 | Alarm Settings #16 |  |  | U16 | 3,16 | 1 | 6
7174 | Alarm Settings #17 |  |  | U16 | 3,16 | 1 | 6
7180 | Alarm Settings #18 |  |  | U16 | 3,16 | 1 | 6
7186 | Alarm Settings #19 |  |  | U16 | 3,16 | 1 | 6
7192 | Alarm Settings #20 |  |  | U16 | 3,16 | 1 | 6
7198 | Alarm Settings #21 |  |  | U16 | 3,16 | 1 | 6
7204 | Alarm Settings #22 |  |  | U16 | 3,16 | 1 | 6
7210 | Alarm Settings #23 |  |  | U16 | 3,16 | 1 | 6
7216 | Alarm Settings #24 |  |  | U16 | 3,16 | 1 | 6
7222 | Alarm Settings #25 |  |  | U16 | 3,16 | 1 | 6
7228 | Alarm Settings #26 |  |  | U16 | 3,16 | 1 | 6
7234 | Alarm Settings #27 |  |  | U16 | 3,16 | 1 | 6
7240 | Alarm Settings #28 |  |  | U16 | 3,16 | 1 | 6
7246 | Alarm Settings #29 |  |  | U16 | 3,16 | 1 | 6
7252 | Alarm Settings #30 |  |  | U16 | 3,16 | 1 | 6
7258 | Alarm Settings #31 |  |  | U16 | 3,16 | 1 | 6
7264 | Alarm Settings #32 |  |  | U16 | 3,16 | 1 | 6
7270 |  |  |  | U16 | 3,16 | 1 | 4
Communication Settings
7274 | device Id |  |  | U16 | 3,16 | 1 | 1
7275 | Modbus TCP Port |  |  | U16 | 3,16 | 1 | 1
7276 | SNTP Mode | 0 : not use, 1 : use |  | U16 | 3,16 | 1 | 1
7277 | SNTP Interval |  | min | U16 | 3,16 | 1 | 1
7278 | Eth#0 IP |  |  | U16 | 3,16 | 1 | 4
7282 | Eth#0 SUBNET |  |  | U16 | 3,16 | 1 | 4
7286 | Eth#0 GATEWAY |  |  | U16 | 3,16 | 1 | 4
7290 | Eth#0 DNS |  |  | U16 | 3,16 | 1 | 4
7294 | SNTP IP |  |  | U16 | 3,16 | 1 | 4
7298 | Host Name |  |  | U16 | 3,16 | 1 | 16
7314 | DAQ server ip |  |  | U16 | 3,16 | 1 | 4
7318 | DHCP enabled |  |  | U16 | 3,16 | 1 | 1
7319 | DAQ sampling rate (0: 2k, 1: 4k, 2: 8k, 3: 16k, 4: 32k) |  |  | U16 | 3,16 | 1 | 1
7320 | DAQ sampling buffer length (0: 2k, 1: 4k, 2: 8k, 3: 16k, 4: 32k, 5: 64) |  |  | U16 | 3,16 | 1 | 1
7321 | DAQ interval (minute) |  |  | U16 | 3,16 | 1 | 1
7322 | DAQ format |  |  | U16 | 3,16 | 1 | 1
7323 | DAQ device id |  |  | U16 | 3,16 | 1 | 1
7324 | DAQ bitspersample (0: 16bit, 1: 32bit) |  |  | U16 | 3,16 | 1 | 1
7325 | reserved |  |  | U16 | 3,16 | 1 | 9
PT #1~9
7334 | Frequency |  |  | U16 | 3,16 | 1 | 1
7335 | feeder count |  |  | U16 | 3,16 | 1 | 1
7336 | #1 wiring mode | 0: not used 1 : 3p4w 2 : 3p3w(2CT), 3 : 3p3w(3CT) 4: 1p2w(L1), 5 : 1p2w(L2), 6 : 1p2w(L3) 7: 1p3w, 8 : SIMULATION |  | U16 | 3,16 | 1 | 1
| #1 reserved |  |  | U16 | 3,16 | 1 | 1
7337 | #1 V nominal |  |  | U32 | 3,16 | 2 | 1
7339 | #1 PT1 |  |  | U32 | 3,16 | 2 | 1
7341 | #1 PT2 |  |  | U16 | 3,16 | 1 | 1
7342 | #1 reserved |  |  | U16 | 3,16 | 1 | 1
7343 | #2 PT |  |  | U16 | 3,16 | 1 | 8
7351 | #3 PT |  |  | U16 | 3,16 | 1 | 8
7359 | #4 PT |  |  | U16 | 3,16 | 1 | 8
7367 | #5 PT |  |  | U16 | 3,16 | 1 | 8
7375 | #6 PT |  |  | U16 | 3,16 | 1 | 8
7383 | #7 PT |  |  | U16 | 3,16 | 1 | 8
7391 | #8 PT |  |  | U16 | 3,16 | 1 | 8
7399 | #9 PT |  |  | U16 | 3,16 | 1 | 8
CT #1~9
7407 | #1 I Nominal |  |  | U16 | 3,16 | 1 | 1
7408 | #1 CT1 |  |  | U16 | 3,16 | 1 | 1
7409 | #1 CT2 | 0: 5A, 1: 100mA/333mV, 2: Rogowski |  | U16 | 3,16 | 1 | 1
7410 | #1 turns |  |  | U16 | 3,16 | 1 | 1
7411 | #1 Starting Current | (1.0 : 0.002*In, 0.5: 0.001*In) 0 ~ 10000 (단위 : mA) |  | U16 | 3,16 | 1 | 1
7412 | #1 CT1 direction | 0: positive, 1: negative |  | U16 | 3,16 | 1 | 1
7413 | #1 CT2 direction |  |  | U16 | 3,16 | 1 | 1
7414 | #1 CT3 direction |  |  | U16 | 3,16 | 1 | 1
7415 | #1 Rogowski CT Model |  |  | U16 | 3,16 | 1 | 1
7416 | #1 phase offset 1 | * phase resolution 60Hz: 0.0211, 50Hz: 0.0176 * range: +63 ~ -383 1.329 ~ -8.079 1.107 ~ -6.732 |  | U16 | 3,16 | 1 | 1
7417 | #1 phase offset 2 |  |  | U16 | 3,16 | 1 | 1
7418 | #1 phase offset 3 |  |  | U16 | 3,16 | 1 | 1
7419 | #1 ZCT Type | 1: 200mV:100mV 2: 200mV:1.5mA 3: 200mV:0.1mA |  | U16 | 3,16 | 1 | 1
7420 | #1 ZCT Scale |  |  | U16 | 3,16 | 1 | 1
7421 | #1 reserved |  |  | U16 | 3,16 | 1 | 2
7423 | #2 CT |  |  | U16 | 3,16 | 1 | 14
7437 | #3 CT |  |  | U16 | 3,16 | 1 | 14
7451 | #4 CT |  |  | U16 | 3,16 | 1 | 14
7465 | #5 CT |  |  | U16 | 3,16 | 1 | 14
7479 | #6 CT |  |  | U16 | 3,16 | 1 | 14
7493 | #7 CT |  |  | U16 | 3,16 | 1 | 14
7507 | #8 CT |  |  | U16 | 3,16 | 1 | 14
7521 | #9 CT |  |  | U16 | 3,16 | 1 | 14
ETC
7535 | VA type | 0: RMS(S=VA) 1: vector(S=sqrt(P*P+Q*Q) |  | U16 | 3,16 | 1 | 1
7536 | PF sign | 0: IEC, 1: IEEE |  | U16 | 3,16 | 1 | 1
7537 | demand interval |  |  | U16 | 3,16 | 1 | 1
7538 | Max. Demand for current TDD(A) - unused |  |  | U16 | 3,16 | 1 | 1
7539 | Target Demand (W) #1~6 |  |  | U32 | 3,16 | 2 | 6
7551 | backlight off time |  |  | U16 | 3,16 | 1 | 1
7552 | brightness |  |  | U16 | 3,16 | 1 | 1
7553 | auto rotation |  |  | U16 | 3,16 | 1 | 1
7554 | Time Zone (~720 ~ 720) | 분단위 |  | S16 | 3,16 | 1 | 1
7555 | max/min reset period | 0: daily 1: weekly 2: monthly |  | U16 | 3,16 | 1 | 1
7556 | TEST MODE | 0 : not use, 1 : use |  | U16 | 3,16 | 1 | 1
7557 | TEST MODE INTERVAL |  |  | U16 | 3,16 | 1 | 1
7558 |  |  |  | U16 |  | 1 | 2
IOM SETTING
7560 | type |  |  | U16 | 3,16 | 1 | 1
7561 | reserved |  |  | U16 | 3,16 | 1 | 3
7564 | DI TYPE #0~3 | 0 : DI, 1 : PI |  | U16 | 3,16 | 1 | 4
7568 | DI debounce #0~3 | 4~255ms |  | U16 | 3,16 | 1 | 4
7572 | PI Scale #0~3 |  |  | U16 | 3,16 | 1 | 4
7576 | reserved |  |  | U16 | 3,16 | 1 | 14
Command
7590 | UTC Time |  |  | U16 | 3,16 | 1 | 4
7594 |  |  |  | U16 | 3,16 | 1 | 6
7600 | reboot |  |  | U16 | 6 | 1 | 1
7601 | save settings |  |  | U16 | 6 | 1 | 1
7602 | Calibration command #1~9 | 0: Enable Calibration 1: U gain 2: I gain 3: W gain 4: Ph gain 5: clear V 6: clear I 7: clear W 8: clear phase 9: IN gain 10: clear IN 11: Disable Calibration 12: save Calibration 13: Upp gain 14: clear Upp gain 15: set dcos 16: clear DcOffset 17: --- 18: --- |  | U16 | 6 | 1 | 9
7611 | V-ref, 1=1V #1~9 |  |  | U16 | 6 | 1 | 9
7620 | I-ref, 1=0.1A #1~9 |  |  | U16 | 6 | 1 | 9
7629 | In-ref, 1=0.1 #1~9 |  |  | U16 | 6 | 1 | 9
7638 | init settings |  |  | U16 | 6 | 1 | 1
7639 | clear PI |  |  | U16 | 6 | 1 | 1
7640 | clear demand #1~9 |  |  | U16 | 6 | 1 | 9
7649 | clear minmax #1~9 |  |  | U16 | 6 | 1 | 9
7658 | clear energy #1~9 |  |  | U16 | 6 | 1 | 9
7667 | clear alarm #1~9 |  |  | U16 | 6 | 1 | 9
7676 | clear event #1~9 |  |  | U16 | 6 | 1 | 9
7685 | load event #1~9 | 1: down, 2:up, 3:top |  | U16 | 6 | 1 | 9
7694 | load alarm #1~9 | 1: down, 2:up, 3:top |  | U16 | 6 | 1 | 9
7703 | Alarm Ack #1~9 | not used |  | U16 | 6 | 1 | 9
7712 | Event Ack #1~9 | not used |  | U16 | 6 | 1 | 9
7721 | DAQ enable #1~9 |  |  | U16 | 6 | 1 | 9
7730 | load itic #1~3 | 1: down, 2:up, 3:top |  | U16 | 6 | 1 | 3
7733 | load itic2 #1~3 | 1: down, 2:up, 3:top |  | U16 | 6 | 1 | 3
7736 | clear ITIC #1~3 |  |  | U16 | 6 | 1 | 3
7739 | reserved |  |  | U16 | 6 | 1

## Alarm Channel
Trend/Alarm Channel
1 | Temp
2 | Freq
3 | U1
4 | U2
5 | U3
6 | U~
7 | U12
8 | U23
9 | U31
10 | Upp~
11 | Voltage Unbalace, Uo
12 | Voltage Unbalace, Uu
13 | I1
14 | I2
15 | I3
16 | I~
17 | Itotal
18 | In
19 | P1
20 | P2
21 | P3
22 | Ptotal
23 | Q1
24 | Q2
25 | Q3
26 | Qtot
27 | D1
28 | D2
29 | D3
30 | D
31 | S1
32 | S2
33 | S3
34 | Stot
35 | PF1
36 | PF2
37 | PF3
38 | PFtot
39 | THD U1
40 | THD U2
41 | THD U3
42 | THD U12
43 | THD U23
44 | THD U31
45 | THD I1
46 | THD I2
47 | THD I3
48 | Dynamic Demand P+
49 | Dynamic Demand P-
50 | Dynamic Demand Q+
51 | Dynamic Demand Q-
52 | Dynamic Demand S
53 | Dynamic Demand I1
54 | Dynamic Demand I2
55 | Dynamic Demand I3
56 | Max. Demand P+
57 | Max. Demand P=-
58 | Max. Demand Q+
59 | Max. Demand Q-
60 | Max. Demand S
61 | Max. Demand I1
62 | Max. Demand I2
63 | Max. Demand I3
64 | Under Deviation U1
65 | Under Deviation U2
66 | Under Deviation U3
67 | Over Drviation U1
68 | Over Drviation U2
69 | Over Drviation U3
70 | CF U1
71 | CF U2
72 | CF U3
73 | CF U12
74 | CF U23
75 | CF U31
76 | CF I1
77 | CF I2
78 | CF I3
79 | KF I1
80 | KF I2
81 | KF I3
82 | PSt 1
83 | PSt 2
84 | PSt 3
85 | Plt 1
86 | Plt 2
87 | Plt 3
88 | Sig. Volt 1
89 | Sig. Volt 2
90 | Sig. Volt 3