## ToDo&Log
2024-12-18 | 1st draft
2026-06-02 | 3ch redefine
2026-06-02

## #1,2,3 Simple
address | Group | name | Decription | 1P | 3P | Unit | Function code | TYPE | 1P | 3P | Word Count | Item Count
Metering
50000 | Common | Time Stamp |  |  |  |  | 3,4 | U32 |  |  | 2 | 1
50002 |  | Heatbit |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50003 |  | HW Model |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50004 |  | HW Version |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50005 |  | FW Version |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50006 |  | FW_BUILD_YEAR |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50007 |  | FW_BUILD_MON |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50008 |  | FW_BUILD_DAY |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50009 |  | Serial Num |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50010 |  | Status |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50011 |  | reserved |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50012 |  | Internal Temp |  |  |  |  | 3,4 | float |  |  | 2 | 1
50014 |  | reserved |  |  |  |  | 3,4 | U32 |  |  | 2 | 3
50020 | #1 | CB Type |  | ● | ● |  | 3,4 | U16 |  |  | 1 | 1
50021 |  | CB Status |  | ● | ● |  | 3,4 | U16 |  |  | 1 | 1
50022 |  | reserved |  | ● | ● |  | 3,4 | U32 |  |  | 2 | 1
50024 |  | Frequency |  | ● | ● | Hz | 3,4 | float |  |  | 2 | 1
50026 |  | U1 | 상전압 1 | ● | ● | V | 3,4 | float |  |  | 2 | 1
50028 |  | U2 | 상전압 2 |  | ● |  | 3,4 | float |  |  | 2 | 1
50030 |  | U3 | 상전압 3 |  | ● |  | 3,4 | float |  |  | 2 | 1
50032 |  | U12 |  |  | ● |  | 3,4 | float |  |  | 2 | 1
50034 |  | U23 |  |  | ● |  | 3,4 | float |  |  | 2 | 1
50036 |  | U31 |  |  | ● |  | 3,4 | float |  |  | 2 | 1
50038 |  | I1 | 상전류 1 | ● | ● | A | 3,4 | float |  |  | 2 | 1
50040 |  | I2 | 상전류 2 |  | ● |  | 3,4 | float |  |  | 2 | 1
50042 |  | I3 | 상전류 3 |  | ● |  | 3,4 | float |  |  | 2 | 1
50044 |  | In | 누설전류 |  | ● |  | 3,4 | float |  |  | 2 | 1
50046 |  | P1 |  | ● | ● | W | 3,4 | float |  |  | 2 | 1
50048 |  | P2 |  |  | ● |  | 3,4 | float |  |  | 2 | 1
50050 |  | P3 |  |  | ● |  | 3,4 | float |  |  | 2 | 1
50052 |  | P total |  | ● | ● |  | 3,4 | float |  |  | 2 | 1
50054 |  | Q total |  | ● | ● | Var | 3,4 | float |  |  | 2 | 1
50056 |  | S total |  | ● | ● | VA | 3,4 | float |  |  | 2 | 1
50058 |  | PF total |  | ● | ● | % | 3,4 | float |  |  | 2 | 1
50060 |  | kWh_imp |  | ● | ● | kWh | 3,4 | U32 |  |  | 2 | 1
50062 |  | kWh_imp_this_month |  | ● | ● | kWh | 3,4 | U32 |  |  | 2 | 1
50064 |  | kWh_imp_last_month |  | ● | ● | kWh | 3,4 | U32 |  |  | 2 | 1
50066 |  | kVARh_imp |  | ● | ● | kVarh | 3,4 | U32 |  |  | 2 | 1
50068 |  | kVAh |  | ● | ● | kVAh | 3,4 | U32 |  |  | 2 | 1
50070 |  | Volt. Unbalance |  | ● | ● | % | 3,4 | float |  |  | 2 | 1
50072 |  | Current Unbalance |  | ● | ● | % | 3,4 | float |  |  | 2 | 1
50074 |  | THD V1 | 고조파함유율 상전압 1 | ● | ● | % | 3,4 | float |  |  | 2 | 1
50076 |  | THD V2 | 고조파함유율 상전압 2 |  | ● | % | 3,4 | float |  |  | 2 | 1
50078 |  | THD V3 | 고조파함유율 상전압 3 |  | ● | % | 3,4 | float |  |  | 2 | 1
50080 |  | THD I1 | 고조파함유율 상전류 1 | ● | ● | % | 3,4 | float |  |  | 2 | 1
50082 |  | THD I2 | 고조파함유율 상전류 2 |  | ● | % | 3,4 | float |  |  | 2 | 1
50084 |  | THD I3 | 고조파함유율 상전류 3 |  | ● | % | 3,4 | float |  |  | 2 | 1
50086 |  | TDD I1 | 디맨드왜형율 상전류 1 | ● | ● | % | 3,4 | float |  |  | 2 | 1
50088 |  | TDD I2 | 디맨드왜형율 상전류 2 |  | ● | % | 3,4 | float |  |  | 2 | 1
50090 |  | TDD I3 | 디맨드왜형율 상전류 3 |  | ● | % | 3,4 | float |  |  | 2 | 1
50092 |  | reserved |  | ● | ● |  | 3,4 | float |  |  | 2 | 4
50100 | #2 |  |  | ● | ● |  | 3,4 | float |  |  | 1 | 80
50180 | #3 |  |  | ● | ● |  | 3,4 | float |  |  | 1 | 80
50260 | #4 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
50340 | #5 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
50420 | #6 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
50500 | #7 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
50580 | #8 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
50660 | #9 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
Harmonics by order
50740 | #1 | Harmonics V1 | 1~41th | ● | ● |  | 3,4 | S16 |  |  | 1 | 41
50781 |  | Harmonics V2 |  |  | ● |  | 3,4 | S16 |  |  | 1 | 41
50822 |  | Harmonics V3 |  |  | ● |  | 3,4 | S16 |  |  | 1 | 41
50863 |  | Harmonics I1 |  | ● | ● |  | 3,4 | S16 |  |  | 1 | 41
50904 |  | Harmonics I2 |  |  | ● |  | 3,4 | S16 |  |  | 1 | 41
50945 |  | Harmonics I3 |  |  | ● |  | 3,4 | S16 |  |  | 1 | 41
50986 | #2 |  |  | ● | ● | [5 empty] | 1 | 246
51232 | #3 |  |  | ● | ● | [5 empty] | 1 | 246
51478 | #4 |  |  | ● | [6 empty] | 1 | 246
51724 | #5 |  |  | ● | [6 empty] | 1 | 246
51970 | #6 |  |  | ● | [6 empty] | 1 | 246
52216 | #7 |  |  | ● | [6 empty] | 1 | 246
52462 | #8 |  |  | ● | [6 empty] | 1 | 246
52708 | #9 |  |  | ● | [6 empty] | 1 | 246

## #1CH modbus
address | name | 설명 | Unit | TYPE | FC | Word Count | Item Count
Metering
0 | Time Stamp |  |  | UTC | 3 | 2 | 1
2 | TYPE |  |  | U16 | 3 | 1 | 1
3 | STATUS | 1 : online, 0 : offline |  | U16 | 3 | 1 | 1
4 | Frequency | 라인주파수 | Hz | float | 3 | 2 | 1
6 | Internal Temp |  | ℃ | float | 3 | 2 | 1
8 | U1 | 상전압 1 | V | float | 3 | 2 | 1
10 | U2 | 상전압 2 |  | float | 3 | 2 | 1
12 | U3 | 상전압 3 |  | float | 3 | 2 | 1
14 | U~ | 상전압 평균 |  | float | 3 | 2 | 1
16 | U12 | 선간 전압 12 |  | float | 3 | 2 | 1
18 | U23 | 선간 전압 23 |  | float | 3 | 2 | 1
20 | U31 | 선간 전압 31 |  | float | 3 | 2 | 1
22 | Upp~ | 선간 전압 평균 |  | float | 3 | 2 | 1
24 | Uunbalance2 |  | % | float | 3 | 2 | 1 | Uu=neg/pos*100
26 | Uunbalance0 |  |  | float | 3 | 2 | 1 | Uo=zero/pos*100
28 | U Zero Sequence Mag. |  |  | float | 3 | 2 | 1
30 | U Zero Sequence angle |  |  | float | 3 | 2 | 1
32 | U Positive Sequence Mag. |  |  | float | 3 | 2 | 1
34 | U Positive Sequence angle |  |  | float | 3 | 2 | 1
36 | U Negative Sequence Mag |  |  | float | 3 | 2 | 1
38 | U Negative Sequence angle |  |  | float | 3 | 2 | 1
40 | Angle U1 |  |  | float | 3 | 2 | 1
42 | Angle U2 |  |  | float | 3 | 2 | 1
44 | Angle U3 |  |  | float | 3 | 2 | 1
46 | U Underdeviation L1 |  | % | float | 3 | 2 | 1
48 | U Underdeviation L2 |  | % | float | 3 | 2 | 1
50 | U Underdeviation L3 |  | % | float | 3 | 2 | 1
52 | U Overdeviation L1 |  | % | float | 3 | 2 | 1
54 | U Overdeviation L2 |  | % | float | 3 | 2 | 1
56 | U Overdeviation L3 |  | % | float | 3 | 2 | 1
58 | I1 | 상전류 1 | A | float | 3 | 2 | 1
60 | I2 | 상전류 2 |  | float | 3 | 2 | 1
62 | I3 | 상전류 3 |  | float | 3 | 2 | 1
64 | I~ |  |  | float | 3 | 2 | 1
66 | I total (I1+I2+I3) |  |  | float | 3 | 2 | 1
68 | In(Measured) |  |  | float | 3 | 2 | 1 | 1. 5A: -3P4W(In) -3P3W(Ig), 2. AT/VT: Ig로 사용
70 | In(Calculated) | Ia+Ib+Ic+In = Ig |  | float | 3 | 2 | 1 | 1. 5A: -3P4W(Ig=Ia+Ib+Ic+In), -3P3W(Ig=Ia+Ib+Ic), 2. AT/VT: 5A와 동일
72 | Ig |  |  | float | 3 | 2 | 1
74 | I Zero Sequence Mag |  |  | float | 3 | 2 | 1
76 | I Zero Sequence angle |  |  | float | 3 | 2 | 1
78 | I Positive Sequence Mag. |  |  | float | 3 | 2 | 1
80 | I Positive Sequence angle |  |  | float | 3 | 2 | 1
82 | I Negative Sequence Mag. |  |  | float | 3 | 2 | 1
84 | I Negative Sequence angle |  |  | float | 3 | 2 | 1
86 | Angle I1 |  |  | float | 3 | 2 | 1
88 | Angle I2 |  |  | float | 3 | 2 | 1
90 | Angle I3 |  |  | float | 3 | 2 | 1
92 | Iunbalance2 |  | % | float | 3 | 2 | 1
94 | Iunbalance0 |  |  | float | 3 | 2 | 1
96 | P1 | 유효전력 P1 | W | float | 3 | 2 | 1
98 | P2 | 유효전력 P2 |  | float | 3 | 2 | 1
100 | P3 | 유효전력 P3 |  | float | 3 | 2 | 1
102 | P total | 유효전력 P-total |  | float | 3 | 2 | 1
104 | fP1 |  |  | float | 3 | 2 | 1
106 | fP2 |  |  | float | 3 | 2 | 1
108 | fP3 |  |  | float | 3 | 2 | 1
110 | fP total |  |  | float | 3 | 2 | 1
112 | Q1 | 무효전력 Q1 | VAR | float | 3 | 2 | 1
114 | Q2 | 무효전력 Q2 |  | float | 3 | 2 | 1
116 | Q3 | 무효전력 Q3 |  | float | 3 | 2 | 1
118 | Q total | 무효전력 Q-total |  | float | 3 | 2 | 1
120 | fQ1 |  |  | float | 3 | 2 | 1
122 | fQ2 |  |  | float | 3 | 2 | 1
124 | fQ3 |  |  | float | 3 | 2 | 1
126 | fQ total |  |  | float | 3 | 2 | 1
128 | S1 | 피상전력 S1 | VA | float | 3 | 2 | 1
130 | S2 | 피상전력 S2 |  | float | 3 | 2 | 1
132 | S3 | 피상전력 S3 |  | float | 3 | 2 | 1
134 | S total | 피상전력 S-total |  | float | 3 | 2 | 1
136 | fS1 |  |  | float | 3 | 2 | 1
138 | fS2 |  |  | float | 3 | 2 | 1
140 | fS3 |  |  | float | 3 | 2 | 1
142 | fS total |  |  | float | 3 | 2 | 1
144 | PF1 | 역률 PF1 | % | float | 3 | 2 | 1
146 | PF2 | 역률 PF2 |  | float | 3 | 2 | 1
148 | PF3 | 역률 PF3 |  | float | 3 | 2 | 1
150 | PF total | 역률 PF-total |  | float | 3 | 2 | 1
152 | dPF1 |  | % | float | 3 | 2 | 1
154 | dPF2 |  |  | float | 3 | 2 | 1
156 | dPF3 |  |  | float | 3 | 2 | 1
158 | dPF total |  |  | float | 3 | 2 | 1
160 | deformed Power D L1 |  | W | float | 3 | 2 | 1 | S=sqrt {P^{2}+Q^{2}+D^{2}}
162 | deformed Power D L2 |  |  | float | 3 | 2 | 1
164 | deformed Power D L3 |  |  | float | 3 | 2 | 1
166 | deformed Power D Total |  |  | float | 3 | 2 | 1
168 | Power Angle(atan(fPt,fQt) L1 |  | Degree | float | 3 | 2 | 1 | Angle between fundamental phase voltage and phase current
170 | Power Angle(atan(fPt,fQt) L2 |  |  | float | 3 | 2 | 1
172 | Power Angle(atan(fPt,fQt) L3 |  |  | float | 3 | 2 | 1
174 |  |  |  | float | 3 | 2 | 1
176 | THD V1 |  | % | float | 3 | 2 | 1
178 | THD V2 |  |  | float | 3 | 2 | 1 | Chip에서 제공하는 결과 사용
180 | THD V3 |  |  | float | 3 | 2 | 1
182 | THD V12 |  |  | float | 3 | 2 | 1
184 | THD V23 |  |  | float | 3 | 2 | 1
186 | THD V31 |  |  | float | 3 | 2 | 1
188 | CF V1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
190 | CF V2 |  |  | float | 3 | 2 | 1
192 | CF V3 |  |  | float | 3 | 2 | 1
194 | CF V12 |  |  | float | 3 | 2 | 1
196 | CF V23 |  |  | float | 3 | 2 | 1
198 | CF V31 |  |  | float | 3 | 2 | 1
200 | THD I1 |  |  | float | 3 | 2 | 1
202 | THD I2 |  |  | float | 3 | 2 | 1
204 | THD I3 |  |  | float | 3 | 2 | 1
206 | TDD I1 |  |  | float | 3 | 2 | 1
208 | TDD I2 |  |  | float | 3 | 2 | 1
210 | TDD I3 |  |  | float | 3 | 2 | 1
212 | K I1 | K-FACTOR : 고조파 허용율 |  | float | 3 | 2 | 1
214 | K I2 |  |  | float | 3 | 2 | 1
216 | K I3 |  |  | float | 3 | 2 | 1
218 | CF I1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
220 | CF I2 |  |  | float | 3 | 2 | 1
222 | CF I3 |  |  | float | 3 | 2 | 1
224 | fU1 | 기본파 U1 | V | float | 3 | 2 | 1
226 | fU2 | 기본파 U2 |  | float | 3 | 2 | 1
228 | fU3 | 기본파 U3 |  | float | 3 | 2 | 1
230 | fU~ | 기본파 전압 평균 |  | float | 3 | 2 | 1
232 | fI1 | 기본파 I1 | A | float | 3 | 2 | 1
234 | fI2 | 기본파 I2 |  | float | 3 | 2 | 1
236 | fI3 | 기본파 I3 |  | float | 3 | 2 | 1
238 | fI~ | 기본파 전류 평균 |  | float | 3 | 2 | 1
Energy
240 | import kwh(0 ~ 999,999,999.9 kw) | 누적 유효전력량 |  | U32 | 3 | 2 | 1
242 | export kwh |  |  | U32 | 3 | 2 | 1
244 | import kvarh |  |  | U32 | 3 | 2 | 1
246 | export kvarh |  |  | U32 | 3 | 2 | 1
248 | kvah |  |  | U32 | 3 | 2 | 1
250 |  |  |  | U32 | 3 | 2 | 1
252 | import kwh this month |  |  | U32 | 3 | 2 | 1
254 | export kwh this month |  |  | U32 | 3 | 2 | 1
256 | import kvarh this month |  |  | U32 | 3 | 2 | 1
258 | export kvarh this month |  |  | U32 | 3 | 2 | 1
260 | kvah this month |  |  | U32 | 3 | 2 | 1
262 |  |  |  | U32 | 3 | 2 | 1
264 | import kwh last month |  |  | U32 | 3 | 2 | 1 | Demand P(import)
266 | export kwh last month |  |  | U32 | 3 | 2 | 1
268 | import kvarh last month |  |  | U32 | 3 | 2 | 1
270 | export kvarh last month |  |  | U32 | 3 | 2 | 1
272 | kvah last month |  |  | U32 | 3 | 2 | 1
274 |  |  |  | U32 | 3 | 2 | 1
276 | import kwh | 0~999,999,999.999 kw |  | U64 | 3 | 4 | 1 | Demand P(import)
280 | export kwh |  |  | U64 | 3 | 4 | 1
284 | import kvarh |  |  | U64 | 3 | 4 | 1
288 | export kvarh |  |  | U64 | 3 | 4 | 1
292 | kvah |  |  | U64 | 3 | 4 | 1
296 |  |  |  | U64 | 3 | 4 | 1
Demand
300 | Time Stamp |  |  | UTC | 3 | 2 | 1
302 | Max Demand P(import) |  |  | float | 3 | 2 | 1
304 | Time Stamp |  |  | UTC | 3 | 2 | 1
306 | Max Demand P(export) |  |  | float | 3 | 2 | 1
308 | Time Stamp |  |  | UTC | 3 | 2 | 1
310 | Max Demand Q(import) |  |  | float | 3 | 2 | 1
312 | Time Stamp |  |  | UTC | 3 | 2 | 1
314 | Max Demand Q(export) |  |  | float | 3 | 2 | 1
316 | Time Stamp |  |  | UTC | 3 | 2 | 1
318 | Max Demand S |  |  | float | 3 | 2 | 1
320 | Time Stamp |  |  | UTC | 3 | 2 | 1
322 | Max Demand I1 |  |  | float | 3 | 2 | 1
324 | Time Stamp |  |  | UTC | 3 | 2 | 1
326 | Max Demand I2 |  |  | float | 3 | 2 | 1
328 | Time Stamp |  |  | UTC | 3 | 2 | 1
330 | Max Demand I3 |  |  | float | 3 | 2 | 1
332 | Demand time stamp |  |  | UTC | 3 | 2 | 1
334 | Demand P(import) |  |  | float | 3 | 2 | 1
336 | Demand P(export) |  |  | float | 3 | 2 | 1 | 최근 24시간 그래프 그린다
338 | Demand Q(import) |  |  | float | 3 | 2 | 1
340 | Demand Q(export) |  |  | float | 3 | 2 | 1
342 | Demand S(export) |  |  | float | 3 | 2 | 1
344 | Demand I1 |  |  | float | 3 | 2 | 1
346 | Demand I2 |  |  | float | 3 | 2 | 1
348 | Demand I3 |  |  | float | 3 | 2 | 1
350 | Present Demand P(import) |  |  | float | 3 | 2 | 1
352 | Present Demand P(export) |  |  | float | 3 | 2 | 1
354 | Present Demand Q(import) |  |  | float | 3 | 2 | 1
356 | Present Demand Q(export) |  |  | float | 3 | 2 | 1
358 | Present Demand S(export) |  |  | float | 3 | 2 | 1
360 | Forecast Demand P(export) |  |  | float | 3 | 2 | 1
362 | Demand P 15m(import) |  |  | float | 3 | 2 | 1
364 |  |  |  | float | 3 | 2 | 1
366 |  |  |  | float | 3 | 2 | 1
368 | Time Stamp(Demand Log 시작일) |  |  | U32 | 3 | 2 | 1
370 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
562 |  |  |  | float | 3 | 2 | 19
Voltage Quality RealTime Value
600 | Voltage Under Deviation L1 |  | % | float | 3 | 2 | 1
602 | Voltage Under Deviation L2 |  | % | float | 3 | 2 | 1
604 | Voltage Under Deviation L3 |  | % | float | 3 | 2 | 1
606 | Voltage Under Value L1 |  | rms | float | 3 | 2 | 1
608 | Voltage Under Value L2 |  | rms | float | 3 | 2 | 1
610 | Voltage Under Value L3 |  | rms | float | 3 | 2 | 1
612 | Voltage Over Deviation L1 |  | % | float | 3 | 2 | 1
614 | Voltage Over Deviation L2 |  | % | float | 3 | 2 | 1
616 | Voltage Over Deviation L3 |  | % | float | 3 | 2 | 1
618 | Voltage Over Value L1 |  | rms | float | 3 | 2 | 1
620 | Voltage Over Value L2 |  | rms | float | 3 | 2 | 1
622 | Voltage Over Value L3 |  | rms | float | 3 | 2 | 1
624 | Flickers Pi L1 | 150/180 Cycles |  | float | 3 | 2 | 1
626 | Flickers Pi L2 |  |  | float | 3 | 2 | 1
628 | Flickers Pi L3 |  |  | float | 3 | 2 | 1
630 | Flicker Pst L1 | 10min |  | float | 3 | 2 | 1
632 | Flicker Pst L2 |  |  | float | 3 | 2 | 1
634 | Flicker Pst L3 |  |  | float | 3 | 2 | 1
636 | Flicker Plt L1 | 2hr |  | float | 3 | 2 | 1 | 최근 24시간 그래프 그린다
638 | Flicker Plt L2 |  |  | float | 3 | 2 | 1
640 | Flicker Plt L3 |  |  | float | 3 | 2 | 1
642 | Signaling Volt L1 | Magnitude of current 10/12 cycles as a percentage of nominal voltage. |  | float | 3 | 2 | 1
644 | Signaling Volt L2 |  |  | float | 3 | 2 | 1
646 | Signaling Volt L3 |  |  | float | 3 | 2 | 1
648 | Signaling Volt Max L1 | Maximum magnitude of MSV from recording started as a percentage of nominal voltage |  | float | 3 | 2 | 1
650 | Signaling Volt Max L2 |  |  | float | 3 | 2 | 1
652 | Signaling Volt Max L3 |  |  | float | 3 | 2 | 1
654 |  |  |  | float | 3 | 2 | 23
EN50160 This Week
700 | start date |  |  | UTC | 3 | 2 | 1
702 | end date |  |  | UTC | 3 | 2 | 1
704 | status&compliance | bit 0: Freq Var1 bit 1: Freq Var2 bit 2: Volt Var1 L1 bit 3: Volt Var1 L2 bit 4: Volt Var1 L3 bit 5: Volt Var2 L1 bit 6: Volt Var2 L2 bit 7: Volt Var2 L3 bit 8: Unbalance bit 9: Volt THD L1 bit 10: Volt THD L2 bit 11: Volt THD L3 bit 12: Volt HD L1 bit 13: Volt HD L2 bit 14: Volt HD L3 bit 15: Pst L1 bit 16: Pst L2 bit 17: Pst L3 bit 18: Plt L1 bit 19: Plt L2 bit 20: Plt L3 bit 21: SigVolt L1 bit 22: SigVolt L2 bit 23: SigVolt L3 bit 31: Complete [status] 0: OK 1: failed |  | U32 | 3 | 2 | 1
706 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1 | 95%/Week
707 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1 | Info Only
708 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
709 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
710 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
711 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
712 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
713 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1 | Info Only
714 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
715 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
716 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
717 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
718 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
719 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
720 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
721 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
722 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
723 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
724 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
725 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
726 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
727 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
728 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
729 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
730 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
731 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1 | 99%/Day
732 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
733 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
734 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
735 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
736 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
737 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
738 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
739 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
740 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
741 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
742 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
743 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
744 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
745 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
746 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
747 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
748 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
749 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
EN50160 Last Week
750 | start date |  |  | UTC | 3 | 2 | 1
752 | end date |  |  | UTC | 3 | 2 | 1
754 | status |  |  | U16 | 3 | 1 | 1
755 | compilance |  |  | U16 | 3 | 1 | 1
756 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1
757 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1
758 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
759 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
760 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1
761 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
762 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
763 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1
764 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
765 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
766 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1
767 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
768 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
769 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1
770 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
771 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
772 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1
773 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
774 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
775 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1
776 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
777 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
778 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1
779 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
780 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
781 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1
782 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
783 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
784 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
785 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
786 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
787 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
788 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
789 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
790 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
791 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
792 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
793 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
794 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
795 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
796 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
797 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
798 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
799 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
Harmonics
800 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
864 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
928 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
992 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
1056 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
1120 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
1184 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
1248 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
1312 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
1376 |  |  |  | S16 | 3 | 1 | 24
Inter Harmonics
1400 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
1464 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
1528 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
1592 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
1656 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
1720 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
1784 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
1848 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
1912 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
1976 |  |  |  | S16 | 3 | 1 | 24
Max/Min
2000 | fr |  |  | U16 | 3 | 1 | 1
2001 | re |  |  | U16 | 3 | 1 | 1
2002 | Reset TimeStamp |  |  | UTC | 3 | 2 | 1
2004 | Frequency |  |  | float | 3 | 2 | 4
2012 | Temp |  |  | float | 3 | 2 | 4
2020 | U1 |  |  | float | 3 | 2 | 4
2028 | U2 |  |  | float | 3 | 2 | 4
2036 | U3 |  |  | float | 3 | 2 | 4 | http://www.relaytech.com/symcomp_calculator.htm
2044 | U~ |  |  | float | 3 | 2 | 4
2052 | U12 |  |  | float | 3 | 2 | 4
2060 | U23 |  |  | float | 3 | 2 | 4
2068 | U31 |  |  | float | 3 | 2 | 4
2076 | Upp~ |  |  | float | 3 | 2 | 4
2084 | I1 |  |  | float | 3 | 2 | 4
2092 | I2 |  |  | float | 3 | 2 | 4
2100 | I3 |  |  | float | 3 | 2 | 4
2108 | I~ |  |  | float | 3 | 2 | 4
2116 | I total |  |  | float | 3 | 2 | 4
2124 | In |  |  | float | 3 | 2 | 4
2132 | Isum |  |  | float | 3 | 2 | 4
2140 | P1 |  |  | float | 3 | 2 | 4
2148 | P2 |  |  | float | 3 | 2 | 4
2156 | P3 |  |  | float | 3 | 2 | 4
2164 | P total |  |  | float | 3 | 2 | 4
2172 | Q1 |  |  | float | 3 | 2 | 4
2180 | Q2 |  |  | float | 3 | 2 | 4
2188 | Q3 |  |  | float | 3 | 2 | 4
2196 | Q total |  |  | float | 3 | 2 | 4
2204 | S1 |  |  | float | 3 | 2 | 4
2212 | S2 |  |  | float | 3 | 2 | 4
2220 | S3 |  |  | float | 3 | 2 | 4
2228 | S total |  |  | float | 3 | 2 | 4
2236 | PF L1 |  |  | float | 3 | 2 | 4
2244 | PF L2 |  |  | float | 3 | 2 | 4
2252 | PF L3 |  |  | float | 3 | 2 | 4
2260 | PF total |  |  | float | 3 | 2 | 4
2268 | THD U1 |  |  | float | 3 | 2 | 4
2276 | THD U2 |  |  | float | 3 | 2 | 4
2284 | THD U3 |  |  | float | 3 | 2 | 4
2292 | THD U12 |  |  | float | 3 | 2 | 4
2300 | THD U23 |  |  | float | 3 | 2 | 4
2308 | THD U31 |  |  | float | 3 | 2 | 4
2316 | THD I1 |  |  | float | 3 | 2 | 4
2324 | THD I2 |  |  | float | 3 | 2 | 4
2332 | THD I3 |  |  | float | 3 | 2 | 4
2340 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
2342 | reserved |  |  | U16 | 3 | 1 | 1
2343 | CRC |  |  | U16 | 3 | 1 | 1
2344 |  |  |  | U16 | 3 | 1 | 6
alarm status
2350 | fr |  |  | U16 | 3 | 1 | 1
2351 | re |  |  | U16 | 3 | 1 | 1
2352 | reset Ts |  |  | UTC | 3 | 2 | 1
2354 | Alarm State #1 | Alarm Channel |  | U16 | 3 | 1 | 1
2355 |  | Alarm Condition |  | U16 | 3 | 1 | 1
2356 |  | Alarm Level |  | float | 3 | 2 | 1
2358 |  | Alarm Status |  | U16 | 3 | 1 | 1
2359 |  | Alarm Count |  | U16 | 3 | 1 | 1
2360 | Alarm State #2 |  |  | U16 | 3 | 1 | 6
2366 | Alarm State #3 |  |  | U16 | 3 | 1 | 6
2372 | Alarm State #4 |  |  | U16 | 3 | 1 | 6
2378 | Alarm State #5 |  |  | U16 | 3 | 1 | 6
2384 | Alarm State #6 |  |  | U16 | 3 | 1 | 6
2390 | Alarm State #7 |  |  | U16 | 3 | 1 | 6
2396 | Alarm State #8 |  |  | U16 | 3 | 1 | 6
2402 | Alarm State #9 |  |  | U16 | 3 | 1 | 6
2408 | Alarm State #10 |  |  | U16 | 3 | 1 | 6
2414 | Alarm State #11 |  |  | U16 | 3 | 1 | 6
2420 | Alarm State #12 |  |  | U16 | 3 | 1 | 6
2426 | Alarm State #13 |  |  | U16 | 3 | 1 | 6
2432 | Alarm State #14 |  |  | U16 | 3 | 1 | 6
2438 | Alarm State #15 |  |  | U16 | 3 | 1 | 6
2444 | Alarm State #16 |  |  | U16 | 3 | 1 | 6
2450 | Alarm State #17 |  |  | U16 | 3 | 1 | 6
2456 | Alarm State #18 |  |  | U16 | 3 | 1 | 6
2462 | Alarm State #19 |  |  | U16 | 3 | 1 | 6
2468 | Alarm State #20 |  |  | U16 | 3 | 1 | 6
2474 | Alarm State #21 |  |  | U16 | 3 | 1 | 6
2480 | Alarm State #22 |  |  | U16 | 3 | 1 | 6
2486 | Alarm State #23 |  |  | U16 | 3 | 1 | 6
2492 | Alarm State #24 |  |  | U16 | 3 | 1 | 6
2498 | Alarm State #25 |  |  | U16 | 3 | 1 | 6
2504 | Alarm State #26 |  |  | U16 | 3 | 1 | 6
2510 | Alarm State #27 |  |  | U16 | 3 | 1 | 6
2516 | Alarm State #28 |  |  | U16 | 3 | 1 | 6
2522 | Alarm State #29 |  |  | U16 | 3 | 1 | 6
2528 | Alarm State #30 |  |  | U16 | 3 | 1 | 6
2534 | Alarm State #31 |  |  | U16 | 3 | 1 | 6
2540 | Alarm State #32 |  |  | U16 | 3 | 1 | 6
2546 | update Ts |  |  | U32 | 3 | 2 | 1
2548 | Global Alarm Status | (alarm 하나라도 있으면 1, 아니면 0) |  | U16 | 3 | 1 | 1
2549 |  |  |  | U16 | 3 | 1 | 1
alarm log
2550 | fr | 0 ~ 1023 |  | U16 | 3 | 1 | 1
2551 | re | 0 ~ 1023 |  | U16 | 3 | 1 | 1
2552 | count | 전체 log 수 |  | U16 | 3 | 1 | 1
2553 | seq |  |  | U16 | 3 | 1 | 1
2554 | Alarm Log #1 | Time Stamp |  | UTC | 3 | 2 | 1 | 2019-5-11변경
2556 |  | status |  | U16 | 3 | 1 | 1
2557 |  | Alarm Channel & Condition |  | U16 | 3 | 1 | 1
2558 |  | level |  | float | 3 | 2 | 1
2560 |  | Value |  | float | 3 | 2 | 1
2562 | Alarm Log #2 |  |  | U16 | 3 | 1 | 8
2570 | Alarm Log #3 |  |  | U16 | 3 | 1 | 8
2578 | Alarm Log #4 |  |  | U16 | 3 | 1 | 8
2586 | Alarm Log #5 |  |  | U16 | 3 | 1 | 8
2594 | Alarm Log #6 |  |  | U16 | 3 | 1 | 8
2602 | Alarm Log #7 |  |  | U16 | 3 | 1 | 8
2610 | Alarm Log #8 |  |  | U16 | 3 | 1 | 8
2618 | Alarm Log #9 |  |  | U16 | 3 | 1 | 8
2626 | Alarm Log #10 |  |  | U16 | 3 | 1 | 8
2634 | Alarm Log #11 |  |  | U16 | 3 | 1 | 8
2642 | Alarm Log #12 |  |  | U16 | 3 | 1 | 8
2650 | Alarm Log #13 |  |  | U16 | 3 | 1 | 8
2658 | Alarm Log #14 |  |  | U16 | 3 | 1 | 8
2666 | Alarm Log #15 |  |  | U16 | 3 | 1 | 8
2674 | Alarm Log #16 |  |  | U16 | 3 | 1 | 8
2682 | Alarm Log #17 |  |  | U16 | 3 | 1 | 8
2690 | Alarm Log #18 |  |  | U16 | 3 | 1 | 8
2698 | Alarm Log #19 |  |  | U16 | 3 | 1 | 8
2706 | Alarm Log #20 |  |  | U16 | 3 | 1 | 8
2714 | Alarm Log #21 |  |  | U16 | 3 | 1 | 8
2722 | Alarm Log #22 |  |  | U16 | 3 | 1 | 8
2730 | Alarm Log #23 |  |  | U16 | 3 | 1 | 8
2738 | Alarm Log #24 |  |  | U16 | 3 | 1 | 8
2746 | Alarm Log #25 |  |  | U16 | 3 | 1 | 8
2754 | Alarm Log #26 |  |  | U16 | 3 | 1 | 8
2762 | Alarm Log #27 |  |  | U16 | 3 | 1 | 8
2770 | Alarm Log #28 |  |  | U16 | 3 | 1 | 8
2778 | Alarm Log #29 |  |  | U16 | 3 | 1 | 8
2786 | Alarm Log #30 |  |  | U16 | 3 | 1 | 8
2794 | Alarm Log #31 |  |  | U16 | 3 | 1 | 8
2802 | Alarm Log #32 |  |  | U16 | 3 | 1 | 8
2810 |  |  |  | U16 | 3 | 1 | 40
이벤트 리스트
2850 | fr | 0 ~ 1023 |  | U16 | 3 | 1 | 1
2851 | re | 0 ~ 1023 |  | U16 | 3 | 1 | 1
2852 | count | 0 ~ 1023 |  | U16 | 3 | 1 | 1
2853 | seq |  |  | U16 | 3 | 1 | 1
PQ 이벤트(Sag, Swell, Transient, OC)
2854 | start ts |  |  | UTC | 3 | 2 | 1
2856 | start ts(ms) |  |  | U16 | 3 | 1 | 1
2857 | duration |  |  | U16 | 3 | 1 | 1
2858 | type | 1 : E_SAG 2 : E_SWELL 3 : E_sINTR 4 : E_lINTR 5 : E_OC 6 : E_RVC 7 : E_TrV 8 : E_TrC |  | U16 | 3 | 1 | 1
2859 | mask |  |  | U16 | 3 | 1 | 1
2860 | Level 1 |  |  | float | 3 | 2 | 1
2862 | Level 2 |  |  | float | 3 | 2 | 1
2864 | Level 3 |  |  | float | 3 | 2 | 1
2866 | PQ Event #2 |  |  | U16 | 3 | 1 | 12
2878 | PQ Event #3 |  |  | U16 | 3 | 1 | 12
2890 | PQ Event #4 |  |  | U16 | 3 | 1 | 12
2902 | PQ Event #5 |  |  | U16 | 3 | 1 | 12
2914 | PQ Event #6 |  |  | U16 | 3 | 1 | 12
2926 | PQ Event #7 |  |  | U16 | 3 | 1 | 12
2938 | PQ Event #8 |  |  | U16 | 3 | 1 | 12
2950 | PQ Event #9 |  |  | U16 | 3 | 1 | 12
2962 | PQ Event #10 |  |  | U16 | 3 | 1 | 12
2974 | PQ Event #11 |  |  | U16 | 3 | 1 | 12
2986 | PQ Event #12 |  |  | U16 | 3 | 1 | 12
2998 | PQ Event #13 |  |  | U16 | 3 | 1 | 12
3010 | PQ Event #14 |  |  | U16 | 3 | 1 | 12
3022 | PQ Event #15 |  |  | U16 | 3 | 1 | 12
3034 | PQ Event #16 |  |  | U16 | 3 | 1 | 12
3046 | PQ Event #17 |  |  | U16 | 3 | 1 | 12
3058 | PQ Event #18 |  |  | U16 | 3 | 1 | 12
3070 | PQ Event #19 |  |  | U16 | 3 | 1 | 12
3082 | PQ Event #20 |  |  | U16 | 3 | 1 | 12
3094 | PQ Event #21 |  |  | U16 | 3 | 1 | 12
3106 | PQ Event #22 |  |  | U16 | 3 | 1 | 12
3118 | PQ Event #23 |  |  | U16 | 3 | 1 | 12
3130 | PQ Event #24 |  |  | U16 | 3 | 1 | 12
3142 | PQ Event #25 |  |  | U16 | 3 | 1 | 12
3154 | PQ Event #26 |  |  | U16 | 3 | 1 | 12
3166 | PQ Event #27 |  |  | U16 | 3 | 1 | 12
3178 | PQ Event #28 |  |  | U16 | 3 | 1 | 12
3190 | PQ Event #29 |  |  | U16 | 3 | 1 | 12
3202 | PQ Event #30 |  |  | U16 | 3 | 1 | 12
3214 | PQ Event #31 |  |  | U16 | 3 | 1 | 12
3226 | PQ Event #32 |  |  | U16 | 3 | 1 | 12
3238 |  |  |  | U16 | 3 | 1 | 2
PQ Event Counter
3240 |  |  |  | U16 | 3 | 1 | 1
3241 |  |  |  | U16 | 3 | 1 | 1
3242 |  |  |  | U16 | 3 | 1 | 1
3243 | Sag Coount |  |  | U16 | 3 | 1 | 1
3244 | Swell Count |  |  | U16 | 3 | 1 | 1
3245 |  |  |  | U16 | 3 | 1 | 1
3246 |  |  |  | U16 | 3 | 1 | 1
3247 |  |  |  | U16 | 3 | 1 | 1
3248 |  |  |  | U16 | 3 | 1 | 1
3249 |  |  |  | U16 | 3 | 1 | 1
Wave Sample | [7 empty] | 32K: 67,107,786 8K: 74,518,668 첫번째 번지 접근시 wave data를 modbus map으로 load 한다
3250 | Wave Form V1 (160 sample) |  |  | S16 | 3 | 1 | 160
3410 | Wave Form V2 (160 sample) |  |  | S16 | 3 | 1 | 160
3570 | Wave Form V3 (160 sample) |  |  | S16 | 3 | 1 | 160
3730 | Wave Form V12 (160 sample) |  |  | S16 | 3 | 1 | 160
3890 | Wave Form V23 (160 sample) |  |  | S16 | 3 | 1 | 160
4050 | Wave Form V31 (160 sample) |  |  | S16 | 3 | 1 | 160
4210 | Wave Form I1 (160 sample) |  |  | S16 | 3 | 1 | 160
4370 | Wave Form I2 (160 sample) |  |  | S16 | 3 | 1 | 160
4530 | Wave Form I3 (160 sample) |  |  | S16 | 3 | 1 | 160
4690 | vscale |  |  | float | 3 | 2 | 1
4692 | iscale |  |  | float | 3 | 2 | 1
4694 |  |  |  | S16 | 3 | 1 | 6
월간리포트 생성위한 10분 평균
4700 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
4702 | U1 |  |  | float | 3 | 2 | 1
4704 | U2 |  |  | float | 3 | 2 | 1
4706 | U3 |  |  | float | 3 | 2 | 1
4708 | U THD1 |  |  | float | 3 | 2 | 1
4710 | U THD2 |  |  | float | 3 | 2 | 1
4712 | U THD3 |  |  | float | 3 | 2 | 1
4714 | Upp THD1 |  |  | float | 3 | 2 | 1
4716 | Upp THD2 |  |  | float | 3 | 2 | 1
4718 | Upp THD3 |  |  | float | 3 | 2 | 1
4720 | U Unbal Uu |  |  | float | 3 | 2 | 1
4722 | U Unbal Uo |  |  | float | 3 | 2 | 1
4724 | I1 |  |  | float | 3 | 2 | 1
4726 | I2 |  |  | float | 3 | 2 | 1
4728 | I3 |  |  | float | 3 | 2 | 1
4730 | In |  |  | float | 3 | 2 | 1
4732 | I THD1 |  |  | float | 3 | 2 | 1
4734 | I THD2 |  |  | float | 3 | 2 | 1
4736 | I THD3 |  |  | float | 3 | 2 | 1
4738 | I TDD1 |  |  | float | 3 | 2 | 1
4740 | I TDD2 |  |  | float | 3 | 2 | 1
4742 | I TDD3 |  |  | float | 3 | 2 | 1
4744 | K-factor 1 |  |  | float | 3 | 2 | 1
4746 | K-factor 2 |  |  | float | 3 | 2 | 1
4748 | K-factor 3 |  |  | float | 3 | 2 | 1
4750 | I Unbal Iu |  |  | float | 3 | 2 | 1
4752 | I Unbal Io |  |  | float | 3 | 2 | 1
4754 | kw imp |  |  | float | 3 | 2 | 1
4756 | kw exp |  |  | float | 3 | 2 | 1
4758 | kvar lag |  |  | float | 3 | 2 | 1
4760 | kvar lead |  |  | float | 3 | 2 | 1
4762 | kVA |  |  | float | 3 | 2 | 1
4764 | PF |  |  | float | 3 | 2 | 1
4766 | dPF |  |  | float | 3 | 2 | 1
4768 | temperature #1 |  |  | float | 3 | 2 | 1
4770 | temperature #2 |  |  | float | 3 | 2 | 1
4772 | temperature #3 |  |  | float | 3 | 2 | 1
4774 | temperature #4 |  |  | float | 3 | 2 | 1
4776 | temperature #5 |  |  | float | 3 | 2 | 1 | *통신이 끊어진 경우 복구를 위해 사용된다
4778 | Harmonics V1 |  |  | S16 | 3 | 1 | 24
4802 | Harmonics V2 |  |  | S16 | 3 | 1 | 24 | demand
4826 | Harmonics V3 |  |  | S16 | 3 | 1 | 24
4850 | Harmonics V12 |  |  | S16 | 3 | 1 | 24
4874 | Harmonics V23 |  |  | S16 | 3 | 1 | 24
4898 | Harmonics V31 |  |  | S16 | 3 | 1 | 24
4922 | Harmonics I1 |  |  | S16 | 3 | 1 | 24
4946 | Harmonics I2 |  |  | S16 | 3 | 1 | 24
4970 | Harmonics I3 |  |  | S16 | 3 | 1 | 24
4994 |  |  |  | U16 | 3 | 1 | 6
Energy log
5000 | Time Stamp |  |  | UTC | 3 | 2 | 1
5002 | kwh import |  |  | float | 3 | 2 | 1
5004 | kvarh lag |  |  | float | 3 | 2 | 1
5006 | kvarh lead |  |  | float | 3 | 2 | 1
5008 | kVAh |  |  | float | 3 | 2 | 1
5010 | energy log last day 01h |  |  | float | 3 | 2 | 4
5018 | energy log last day 02h |  |  | float | 3 | 2 | 4
5026 | energy log last day 03h |  |  | float | 3 | 2 | 4
5034 | energy log last day 04h |  |  | float | 3 | 2 | 4
5042 | energy log last day 05h |  |  | float | 3 | 2 | 4
5050 | energy log last day 06h |  |  | float | 3 | 2 | 4
5058 | energy log last day 07h |  |  | float | 3 | 2 | 4
5066 | energy log last day 08h |  |  | float | 3 | 2 | 4
5074 | energy log last day 09h |  |  | float | 3 | 2 | 4
5082 | energy log last day 10h |  |  | float | 3 | 2 | 4
5090 | energy log last day 11h |  |  | float | 3 | 2 | 4
5098 | energy log last day 12h |  |  | float | 3 | 2 | 4
5106 | energy log last day 13h |  |  | float | 3 | 2 | 4
5114 | energy log last day 14h |  |  | float | 3 | 2 | 4
5122 | energy log last day 15h |  |  | float | 3 | 2 | 4
5130 | energy log last day 16h |  |  | float | 3 | 2 | 4
5138 | energy log last day 17h |  |  | float | 3 | 2 | 4
5146 | energy log last day 18h |  |  | float | 3 | 2 | 4
5154 | energy log last day 19h |  |  | float | 3 | 2 | 4
5162 | energy log last day 20h |  |  | float | 3 | 2 | 4
5170 | energy log last day 21h |  |  | float | 3 | 2 | 4
5178 | energy log last day 22h |  |  | float | 3 | 2 | 4
5186 | energy log last day 23h |  |  | float | 3 | 2 | 4
5194 |  |  |  | U16 | 3 | 1 | 6
5200 | Time Stamp |  |  | UTC | 3 | 2 | 1
5202 | kwh import |  |  | float | 3 | 2 | 1
5204 | kvarh lag |  |  | float | 3 | 2 | 1
5206 | kvarh lead |  |  | float | 3 | 2 | 1
5208 | kVAh |  |  | float | 3 | 2 | 1
5210 | energy log this day 01h |  |  | float | 3 | 2 | 4
5218 | energy log this day 02h |  |  | float | 3 | 2 | 4
5226 | energy log this day 03h |  |  | float | 3 | 2 | 4
5234 | energy log this day 04h |  |  | float | 3 | 2 | 4
5242 | energy log this day 05h |  |  | float | 3 | 2 | 4
5250 | energy log this day 06h |  |  | float | 3 | 2 | 4
5258 | energy log this day 07h |  |  | float | 3 | 2 | 4
5266 | energy log this day 08h |  |  | float | 3 | 2 | 4
5274 | energy log this day 09h |  |  | float | 3 | 2 | 4
5282 | energy log this day 10h |  |  | float | 3 | 2 | 4
5290 | energy log this day 11h |  |  | float | 3 | 2 | 4
5298 | energy log this day 12h |  |  | float | 3 | 2 | 4
5306 | energy log this day 13h |  |  | float | 3 | 2 | 4
5314 | energy log this day 14h |  |  | float | 3 | 2 | 4 | 전일 디멘트 로그
5322 | energy log this day 15h |  |  | float | 3 | 2 | 4
5330 | energy log this day 16h |  |  | float | 3 | 2 | 4
5338 | energy log this day 17h |  |  | float | 3 | 2 | 4
5346 | energy log this day 18h |  |  | float | 3 | 2 | 4
5354 | energy log this day 19h |  |  | float | 3 | 2 | 4
5362 | energy log this day 20h |  |  | float | 3 | 2 | 4
5370 | energy log this day 21h |  |  | float | 3 | 2 | 4
5378 | energy log this day 22h |  |  | float | 3 | 2 | 4
5386 | energy log this day 23h |  |  | float | 3 | 2 | 4
5394 |  |  |  | U16 | 3 | 1 | 6
demand log last day
5400 | Time Stamp |  |  | U32 | 3 | 2 | 1
5402 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
5594 |  |  |  | U16 | 3 | 1 | 6
Max/Min last data
5600 | fr |  |  | S16 | 3 | 1 | 1
5601 | re |  |  | S16 | 3 | 1 | 1
5602 | Reset TimeStamp |  |  | UTC | 3 | 2 | 1
5604 | Frequency |  |  | float | 3 | 2 | 4
5612 | Temp |  |  | float | 3 | 2 | 4
5620 | U1 |  |  | float | 3 | 2 | 4
5628 | U2 |  |  | float | 3 | 2 | 4
5636 | U3 |  |  | float | 3 | 2 | 4
5644 | U~ |  |  | float | 3 | 2 | 4
5652 | U12 |  |  | float | 3 | 2 | 4
5660 | U23 |  |  | float | 3 | 2 | 4
5668 | U31 |  |  | float | 3 | 2 | 4
5676 | Upp~ |  |  | float | 3 | 2 | 4
5684 | I1 |  |  | float | 3 | 2 | 4
5692 | I2 |  |  | float | 3 | 2 | 4
5700 | I3 |  |  | float | 3 | 2 | 4
5708 | I~ |  |  | float | 3 | 2 | 4
5716 | I total |  |  | float | 3 | 2 | 4
5724 | In |  |  | float | 3 | 2 | 4
5732 | Isum |  |  | float | 3 | 2 | 4
5740 | P1 |  |  | float | 3 | 2 | 4
5748 | P2 |  |  | float | 3 | 2 | 4
5756 | P3 |  |  | float | 3 | 2 | 4
5764 | P total |  |  | float | 3 | 2 | 4
5772 | Q1 |  |  | float | 3 | 2 | 4
5780 | Q2 |  |  | float | 3 | 2 | 4
5788 | Q3 |  |  | float | 3 | 2 | 4
5796 | Q total |  |  | float | 3 | 2 | 4
5804 | S1 |  |  | float | 3 | 2 | 4
5812 | S2 |  |  | float | 3 | 2 | 4
5820 | S3 |  |  | float | 3 | 2 | 4
5828 | S total |  |  | float | 3 | 2 | 4
5836 | PF L1 |  |  | float | 3 | 2 | 4
5844 | PF L2 |  |  | float | 3 | 2 | 4
5852 | PF L3 |  |  | float | 3 | 2 | 4
5860 | PF total |  |  | float | 3 | 2 | 4
5868 | THD U1 |  |  | float | 3 | 2 | 4
5876 | THD U2 |  |  | float | 3 | 2 | 4
5884 | THD U3 |  |  | float | 3 | 2 | 4
5892 | THD U12 |  |  | float | 3 | 2 | 4
5900 | THD U23 |  |  | float | 3 | 2 | 4
5908 | THD U31 |  |  | float | 3 | 2 | 4
5916 | THD I1 |  |  | float | 3 | 2 | 4
5924 | THD I2 |  |  | float | 3 | 2 | 4
5932 | THD I3 |  |  | float | 3 | 2 | 4
5940 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
5942 | reserved |  |  | U16 | 3 | 1 | 1
5943 | CRC |  |  | U16 | 3 | 1 | 1
5944 |  |  |  | U16 | 3 | 1 | 6
ITIC
5950 | fr |  |  | U16 | 3 | 1 | 1
5951 | re |  |  | U16 | 3 | 1 | 1
5952 | count |  |  | U16 | 3 | 1 | 1
5953 | SEQ |  |  | U16 | 3 | 1 | 1
5954 | Log #1 | start ts |  | UTC | 3 | 2 | 1
5956 |  | start ts(ms) |  | U16 | 3 | 1 | 1
5957 |  | duration |  | U16 | 3 | 1 | 1
5958 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
5959 |  | mask |  | U16 | 3 | 1 | 1
5960 |  | Level 1 |  | float | 3 | 2 | 1
5962 |  | Level 2 |  | float | 3 | 2 | 1
5964 |  | Level 3 |  | float | 3 | 2 | 1
5966 |  | Normal |  | float | 3 | 2 | 1
5968 | Log #2 |  |  | U16 | 3 | 1 | 14
5982 | Log #3 |  |  | U16 | 3 | 1 | 14
5996 | Log #4 |  |  | U16 | 3 | 1 | 14
6010 | Log #5 |  |  | U16 | 3 | 1 | 14
6024 | Log #6 |  |  | U16 | 3 | 1 | 14
6038 | Log #7 |  |  | U16 | 3 | 1 | 14
6052 | Log #8 |  |  | U16 | 3 | 1 | 14
6066 | Log #9 |  |  | U16 | 3 | 1 | 14
6080 | Log #10 |  |  | U16 | 3 | 1 | 14
6094 | Log #11 |  |  | U16 | 3 | 1 | 14
6108 | Log #12 |  |  | U16 | 3 | 1 | 14
6122 | Log #13 |  |  | U16 | 3 | 1 | 14
6136 | Log #14 |  |  | U16 | 3 | 1 | 14
6150 | Log #15 |  |  | U16 | 3 | 1 | 14
6164 | Log #16 |  |  | U16 | 3 | 1 | 14
6178 | Log #17 |  |  | U16 | 3 | 1 | 14
6192 | Log #18 |  |  | U16 | 3 | 1 | 14
6206 | Log #19 |  |  | U16 | 3 | 1 | 14
6220 | Log #20 |  |  | U16 | 3 | 1 | 14
6234 | Log #21 |  |  | U16 | 3 | 1 | 14
6248 | Log #22 |  |  | U16 | 3 | 1 | 14
6262 | Log #23 |  |  | U16 | 3 | 1 | 14
6276 | Log #24 |  |  | U16 | 3 | 1 | 14
6290 | Log #25 |  |  | U16 | 3 | 1 | 14
6304 | Log #26 |  |  | U16 | 3 | 1 | 14
6318 | Log #27 |  |  | U16 | 3 | 1 | 14
6332 | Log #28 |  |  | U16 | 3 | 1 | 14
6346 | Log #29 |  |  | U16 | 3 | 1 | 14
6360 | Log #30 |  |  | U16 | 3 | 1 | 14
6374 | Log #31 |  |  | U16 | 3 | 1 | 14
6388 | Log #32 |  |  | U16 | 3 | 1 | 14
6402 |  |  |  | U16 | 3 | 1 | 8
ITIC(Configurator)
6410 | fr |  |  | U16 | 3 | 1 | 1
6411 | re |  |  | U16 | 3 | 1 | 1
6412 | count |  |  | U16 | 3 | 1 | 1
6413 | reserved |  |  | U16 | 3 | 1 | 1
6414 | Log #1 | start ts |  | UTC | 3 | 2 | 1
6416 |  | start ts(ms) |  | U16 | 3 | 1 | 1
6417 |  | duration |  | U16 | 3 | 1 | 1
6418 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
6419 |  | mask |  | U16 | 3 | 1 | 1
6420 |  | Level 1 |  | float | 3 | 2 | 1
6422 |  | Level 2 |  | float | 3 | 2 | 1
6424 |  | Level 3 |  | float | 3 | 2 | 1
6426 |  | Normal |  | float | 3 | 2 | 1
6428 | Log #2 |  |  | U16 | 3 | 1 | 14
6442 | Log #3 |  |  | U16 | 3 | 1 | 14
6456 | Log #4 |  |  | U16 | 3 | 1 | 14
6470 | Log #5 |  |  | U16 | 3 | 1 | 14
6484 | Log #6 |  |  | U16 | 3 | 1 | 14
6498 | Log #7 |  |  | U16 | 3 | 1 | 14
6512 | Log #8 |  |  | U16 | 3 | 1 | 14
6526 | Log #9 |  |  | U16 | 3 | 1 | 14
6540 | Log #10 |  |  | U16 | 3 | 1 | 14
6554 | Log #11 |  |  | U16 | 3 | 1 | 14
6568 | Log #12 |  |  | U16 | 3 | 1 | 14
6582 | Log #13 |  |  | U16 | 3 | 1 | 14
6596 | Log #14 |  |  | U16 | 3 | 1 | 14
6610 | Log #15 |  |  | U16 | 3 | 1 | 14
6624 | Log #16 |  |  | U16 | 3 | 1 | 14
6638 | Log #17 |  |  | U16 | 3 | 1 | 14
6652 | Log #18 |  |  | U16 | 3 | 1 | 14
6666 | Log #19 |  |  | U16 | 3 | 1 | 14
6680 | Log #20 |  |  | U16 | 3 | 1 | 14
6694 | Log #21 |  |  | U16 | 3 | 1 | 14
6708 | Log #22 |  |  | U16 | 3 | 1 | 14
6722 | Log #23 |  |  | U16 | 3 | 1 | 14
6736 | Log #24 |  |  | U16 | 3 | 1 | 14
6750 | Log #25 |  |  | U16 | 3 | 1 | 14
6764 | Log #26 |  |  | U16 | 3 | 1 | 14
6778 | Log #27 |  |  | U16 | 3 | 1 | 14
6792 | Log #28 |  |  | U16 | 3 | 1 | 14
6806 | Log #29 |  |  | U16 | 3 | 1 | 14
6820 | Log #30 |  |  | U16 | 3 | 1 | 14
6834 | Log #31 |  |  | U16 | 3 | 1 | 14
6848 | Log #32 |  |  | U16 | 3 | 1 | 14
6862 |  |  |  | U16 | 3 | 1 | 8
Setting 영역 시작
PQ Event
6870 | OC Level | 정격의 2배 |  | U16 | 3,16 | 1 | 1
6871 | OC Cycle | unused |  | U16 | 3,16 | 1 | 1
6872 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
6873 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
6874 |  |  |  | U16 | 3,16 | 1 | 2
6876 | Sag Level(%), 90% | < 90% |  | U16 | 3,16 | 1 | 1
6877 | Sag Cycle | unused |  | U16 | 3,16 | 1 | 1
6878 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
6879 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
6880 |  |  |  | U16 | 3,16 | 1 | 2
6882 | Swell Level(%), 110~200~ | > 110% |  | U16 | 3,16 | 1 | 1
6883 | Swell Cycle | unused |  | U16 | 3,16 | 1 | 1
6884 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
6885 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
6886 |  |  |  | U16 | 3,16 | 1 | 2
6888 | Interruption Level, 5% | < 5% |  | U16 | 3,16 | 1 | 1
6889 | Interruption Time, 60s | unused |  | U16 | 3,16 | 1 | 1
6890 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
6891 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
6892 |  |  |  | U16 | 3,16 | 1 | 2
Transient Trigger
6894 | Transient Voltage, HoldOff Time, 20ms | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
6895 | Transient Voltage, Absolute Peak Level, 200% | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
6896 | Transient Voltage, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
6897 | Transient Voltage, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
6898 | Transient Current, HoldOff Time | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
6899 | Transient Current, Absolute Peak Level | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
6900 | Transient Current, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
6901 | Transient Current, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
6902 |  |  |  | U16 | 3,16 | 1 | 12
Recorder
Waveform
6914 | Recorder resolution(32k, 8k) |  |  | U16 | 3,16 | 1 | 1
6915 | Recorded paramater (U or I) |  |  | U16 | 3,16 | 1 | 1
6916 | pre trigger time(0.1s) |  |  | U16 | 3,16 | 1 | 1
6917 | post trigger time(1s) |  |  | U16 | 3,16 | 1 | 1
Disturbance
6918 | Recorder resolution (Half Cycle) |  |  | U16 | 3,16 | 1 | 1
6919 | Recorded parametrs(U or I) |  |  | U16 | 3,16 | 1 | 1
6920 | pre trigger time(100 sample) |  |  | U16 | 3,16 | 1 | 1
6921 | post trigger time(900 sample) |  |  | U16 | 3,16 | 1 | 1
6922 |  |  |  | U16 | 3,16 | 1 | 12
Trend Recorder
6934 | Trend Group #1 Active |  |  | U16 | 3,16 | 1 | 1
6935 | Trend Group #1 Storage Interval |  |  | U16 | 3,16 | 1 | 1
6936 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
6937 | Trend Group #1, Channel #1 |  |  | U16 | 3,16 | 1 | 1
6938 | Trend Group #1, Channel #2 |  |  | U16 | 3,16 | 1 | 1
6939 | Trend Group #1, Channel #3 |  |  | U16 | 3,16 | 1 | 1
6940 | Trend Group #1, Channel #4 |  |  | U16 | 3,16 | 1 | 1
6941 | Trend Group #1, Channel #5 |  |  | U16 | 3,16 | 1 | 1
6942 | Trend Group #1, Channel #6 |  |  | U16 | 3,16 | 1 | 1
6943 | Trend Group #1, Channel #7 |  |  | U16 | 3,16 | 1 | 1
6944 | Trend Group #1, Channel #8 |  |  | U16 | 3,16 | 1 | 1
6945 | Trend Group #1, Channel #9 |  |  | U16 | 3,16 | 1 | 1
6946 | Trend Group #1, Channel #10 |  |  | U16 | 3,16 | 1 | 1
6947 | Trend Group #1, Channel #11 |  |  | U16 | 3,16 | 1 | 1
6948 | Trend Group #1, Channel #12 |  |  | U16 | 3,16 | 1 | 1
6949 | Trend Group #1, Channel #13 |  |  | U16 | 3,16 | 1 | 1
6950 | Trend Group #1, Channel #14 |  |  | U16 | 3,16 | 1 | 1
6951 | Trend Group #1, Channel #15 |  |  | U16 | 3,16 | 1 | 1
6952 | Trend Group #1, Channel #16 |  |  | U16 | 3,16 | 1 | 1
6953 | Trend Group #2 Active |  |  | U16 | 3,16 | 1 | 1
6954 | Trend Group #2 Storage Interval |  |  | U16 | 3,16 | 1 | 1
6955 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
6956 | Trend Group #2, Channel #1 |  |  | U16 | 3,16 | 1 | 1
6957 | Trend Group #2, Channel #2 |  |  | U16 | 3,16 | 1 | 1
6958 | Trend Group #2, Channel #3 |  |  | U16 | 3,16 | 1 | 1
6959 | Trend Group #2, Channel #4 |  |  | U16 | 3,16 | 1 | 1
6960 | Trend Group #2, Channel #5 |  |  | U16 | 3,16 | 1 | 1
6961 | Trend Group #2, Channel #6 |  |  | U16 | 3,16 | 1 | 1
6962 | Trend Group #2, Channel #7 |  |  | U16 | 3,16 | 1 | 1
6963 | Trend Group #2, Channel #8 |  |  | U16 | 3,16 | 1 | 1
6964 | Trend Group #2, Channel #9 |  |  | U16 | 3,16 | 1 | 1
6965 | Trend Group #2, Channel #10 |  |  | U16 | 3,16 | 1 | 1
6966 | Trend Group #2, Channel #11 |  |  | U16 | 3,16 | 1 | 1
6967 | Trend Group #2, Channel #12 |  |  | U16 | 3,16 | 1 | 1
6968 | Trend Group #2, Channel #13 |  |  | U16 | 3,16 | 1 | 1
6969 | Trend Group #2, Channel #14 |  |  | U16 | 3,16 | 1 | 1
6970 | Trend Group #2, Channel #15 |  |  | U16 | 3,16 | 1 | 1
6971 | Trend Group #2, Channel #16 |  |  | U16 | 3,16 | 1 | 1
6972 | Trend Group #3 Active |  |  | U16 | 3,16 | 1 | 1
6973 | Trend Group #3 Storage Interval |  |  | U16 | 3,16 | 1 | 1
6974 |  |  |  | U16 | 3,16 | 1 | 1
6975 | Trend Group #3, Channel #1 |  |  | U16 | 3,16 | 1 | 1
6976 | Trend Group #3, Channel #2 |  |  | U16 | 3,16 | 1 | 1
6977 | Trend Group #3, Channel #3 |  |  | U16 | 3,16 | 1 | 1
6978 | Trend Group #3, Channel #4 |  |  | U16 | 3,16 | 1 | 1
6979 | Trend Group #3, Channel #5 |  |  | U16 | 3,16 | 1 | 1
6980 | Trend Group #3, Channel #6 |  |  | U16 | 3,16 | 1 | 1
6981 | Trend Group #3, Channel #7 |  |  | U16 | 3,16 | 1 | 1
6982 | Trend Group #3, Channel #8 |  |  | U16 | 3,16 | 1 | 1
6983 | Trend Group #3, Channel #9 |  |  | U16 | 3,16 | 1 | 1
6984 | Trend Group #3, Channel #10 |  |  | U16 | 3,16 | 1 | 1
6985 | Trend Group #3, Channel #11 |  |  | U16 | 3,16 | 1 | 1
6986 | Trend Group #3, Channel #12 |  |  | U16 | 3,16 | 1 | 1
6987 | Trend Group #3, Channel #13 |  |  | U16 | 3,16 | 1 | 1
6988 | Trend Group #3, Channel #14 |  |  | U16 | 3,16 | 1 | 1
6989 | Trend Group #3, Channel #15 |  |  | U16 | 3,16 | 1 | 1
6990 | Trend Group #3, Channel #16 |  |  | U16 | 3,16 | 1 | 1
6991 | Trend Group #4 Active |  |  | U16 | 3,16 | 1 | 1
6992 | Trend Group #4 Storage Interval |  |  | U16 | 3,16 | 1 | 1
6993 |  |  |  | U16 | 3,16 | 1 | 1
6994 | Trend Group #4, Channel #1 |  |  | U16 | 3,16 | 1 | 1
6995 | Trend Group #4, Channel #2 |  |  | U16 | 3,16 | 1 | 1
6996 | Trend Group #4, Channel #3 |  |  | U16 | 3,16 | 1 | 1
6997 | Trend Group #4, Channel #4 |  |  | U16 | 3,16 | 1 | 1
6998 | Trend Group #4, Channel #5 |  |  | U16 | 3,16 | 1 | 1
6999 | Trend Group #4, Channel #6 |  |  | U16 | 3,16 | 1 | 1
7000 | Trend Group #4, Channel #7 |  |  | U16 | 3,16 | 1 | 1
7001 | Trend Group #4, Channel #8 |  |  | U16 | 3,16 | 1 | 1
7002 | Trend Group #4, Channel #9 |  |  | U16 | 3,16 | 1 | 1
7003 | Trend Group #4, Channel #10 |  |  | U16 | 3,16 | 1 | 1
7004 | Trend Group #4, Channel #11 |  |  | U16 | 3,16 | 1 | 1
7005 | Trend Group #4, Channel #12 |  |  | U16 | 3,16 | 1 | 1
7006 | Trend Group #4, Channel #13 |  |  | U16 | 3,16 | 1 | 1
7007 | Trend Group #4, Channel #14 |  |  | U16 | 3,16 | 1 | 1
7008 | Trend Group #4, Channel #15 |  |  | U16 | 3,16 | 1 | 1
7009 | Trend Group #4, Channel #16 |  |  | U16 | 3,16 | 1 | 1
7010 |  |  |  | U16 | 3,16 | 1 | 4
Power Quality Report
7014 | Active |  |  | U16 | 3,16 | 1 | 1
7015 | Start Day |  |  | U16 | 3,16 | 1 | 1
7016 |  |  |  | U16 |  | 1 | 8
Alarm Definition
7024 | compare Time Delay(1s) |  |  | U16 | 3,16 | 1 | 1
7025 |  |  |  | U16 |  | 1 | 1
7026 |  |  |  | U16 |  | 1 | 1
7027 |  |  |  | U16 |  | 1 | 1
Alarm Settings
7028 | Alarm Info #1 Channel(0:disabled, >0: enabled) |  |  | U16 | 3,16 | 1 | 1
7029 | Alarm Cond (0: < , 1:>) |  |  | U16 | 3,16 | 1 | 1
7030 | Hysteresis (% of Nominal) |  |  | U16 | 3,16 | 1 | 1
7031 | Alarm Action (None, Relay or Beep) |  |  | U16 | 3,16 | 1 | 1
7032 | Alarm Level |  |  | float | 3,16 | 2 | 1
7034 | Alarm Settings #2 |  |  | U16 | 3,16 | 1 | 6
7040 | Alarm Settings #3 |  |  | U16 | 3,16 | 1 | 6
7046 | Alarm Settings #4 |  |  | U16 | 3,16 | 1 | 6
7052 | Alarm Settings #5 |  |  | U16 | 3,16 | 1 | 6
7058 | Alarm Settings #6 |  |  | U16 | 3,16 | 1 | 6
7064 | Alarm Settings #7 |  |  | U16 | 3,16 | 1 | 6
7070 | Alarm Settings #8 |  |  | U16 | 3,16 | 1 | 6
7076 | Alarm Settings #9 |  |  | U16 | 3,16 | 1 | 6
7082 | Alarm Settings #10 |  |  | U16 | 3,16 | 1 | 6
7088 | Alarm Settings #11 |  |  | U16 | 3,16 | 1 | 6
7094 | Alarm Settings #12 |  |  | U16 | 3,16 | 1 | 6
7100 | Alarm Settings #13 |  |  | U16 | 3,16 | 1 | 6
7106 | Alarm Settings #14 |  |  | U16 | 3,16 | 1 | 6
7112 | Alarm Settings #15 |  |  | U16 | 3,16 | 1 | 6
7118 | Alarm Settings #16 |  |  | U16 | 3,16 | 1 | 6
7124 | Alarm Settings #17 |  |  | U16 | 3,16 | 1 | 6
7130 | Alarm Settings #18 |  |  | U16 | 3,16 | 1 | 6
7136 | Alarm Settings #19 |  |  | U16 | 3,16 | 1 | 6
7142 | Alarm Settings #20 |  |  | U16 | 3,16 | 1 | 6
7148 | Alarm Settings #21 |  |  | U16 | 3,16 | 1 | 6
7154 | Alarm Settings #22 |  |  | U16 | 3,16 | 1 | 6
7160 | Alarm Settings #23 |  |  | U16 | 3,16 | 1 | 6
7166 | Alarm Settings #24 |  |  | U16 | 3,16 | 1 | 6
7172 | Alarm Settings #25 |  |  | U16 | 3,16 | 1 | 6
7178 | Alarm Settings #26 |  |  | U16 | 3,16 | 1 | 6
7184 | Alarm Settings #27 |  |  | U16 | 3,16 | 1 | 6
7190 | Alarm Settings #28 |  |  | U16 | 3,16 | 1 | 6
7196 | Alarm Settings #29 |  |  | U16 | 3,16 | 1 | 6
7202 | Alarm Settings #30 |  |  | U16 | 3,16 | 1 | 6
7208 | Alarm Settings #31 |  |  | U16 | 3,16 | 1 | 6
7214 | Alarm Settings #32 |  |  | U16 | 3,16 | 1 | 6
IOM Data
7220 | DI status #0 |  |  | U16 | 3 | 1 | 1
7221 | DI status #1 |  |  | U16 | 3 | 1 | 1
7222 | DI status #2 |  |  | U16 | 3 | 1 | 1
7223 | DI status #3 |  |  | U16 | 3 | 1 | 1
7224 | DI Pulse Data #0 |  |  | U32 | 3 | 2 | 1
7226 | DI Pulse Data #1 |  |  | U32 | 3 | 2 | 1
7228 | DI Pulse Data #2 |  |  | U32 | 3 | 2 | 1
7230 | DI Pulse Data #3 |  |  | U32 | 3 | 2 | 1
7232 | TEMP #0 |  |  | float | 3 | 2 | 1
7234 | TEMP #1 |  |  | float | 3 | 2 | 1
7236 | TEMP #2 |  |  | float | 3 | 2 | 1
7238 | TEMP #3 |  |  | float | 3 | 2 | 1
METER INFO
7240 | serial# |  |  | U16 | 3 | 1 | 6
7246 | MAC MSB |  |  | U16 | 3 | 1 | 2
7248 | mac address |  |  | U16 | 3 | 1 | 4
7252 | IP ADDR |  |  | U16 | 3 | 1 | 4
7256 | HW Model |  |  | U16 | 3 | 1 | 1
7257 | HW version |  |  | U16 | 3 | 1 | 1
7258 | FW version |  |  | U16 | 3 | 1 | 1
7259 | FW_BUILD_YEAR |  |  | U16 | 3 | 1 | 1
7260 | FW_BUILD_MON |  |  | U16 | 3 | 1 | 1
7261 | FW_BUILD_DAY |  |  | U16 | 3 | 1 | 1
7262 | HEART BIT |  |  | U16 | 3 | 1 | 1
7263 | MODBUS RX COUNT |  |  | U16 | 3 | 1 | 1
7264 | ALARM STS |  |  | U16 | 3 | 1 | 1
7265 | EVENT STS |  |  | U16 | 3 | 1 | 1
7266 | RSTP STS[0~1] |  |  | U16 | 3 | 1 | 2
7268 | SNTP STS |  |  | U16 | 3 | 1 | 1
7269 | DEV STS |  |  | U16 | 3 | 1 | 1
7270 | NET STS |  |  | U16 | 3 | 1 | 1
7271 | TOT STS |  |  | U16 | 3 | 1 | 1
7262 | reserved |  |  | U16 | 3 | 1 | 8
Communication Settings
7270 | device Id |  |  | U16 | 3,16 | 1 | 1
7271 | Modbus TCP Port |  |  | U16 | 3,16 | 1 | 1
7272 | SNTP Mode | 0 : not use, 1 : use |  | U16 | 3,16 | 1 | 1
7273 | SNTP Interval |  | min | U16 | 3,16 | 1 | 1
7274 | Eth#0 IP |  |  | U16 | 3,16 | 1 | 4
7278 | Eth#0 SUBNET |  |  | U16 | 3,16 | 1 | 4
7282 | Eth#0 GATEWAY |  |  | U16 | 3,16 | 1 | 4
7286 | Eth#0 DNS |  |  | U16 | 3,16 | 1 | 4
7290 | SNTP IP |  |  | U16 | 3,16 | 1 | 4
7294 | Host Name |  |  | U16 | 3,16 | 1 | 16
7310 | DAQ server ip |  |  | U16 | 3,16 | 1 | 4
7314 | DHCP enabled |  |  | U16 | 3,16 | 1 | 1
7315 | DAQ sampling rate (0: 2k, 1: 4k, 2: 8k, 3: 16k, 4: 32k) |  |  | U16 | 3,16 | 1 | 1
7316 | DAQ sampling buffer length (0: 2k, 1: 4k, 2: 8k, 3: 16k, 4: 32k, 5: 64) |  |  | U16 | 3,16 | 1 | 1
7317 | DAQ interval (minute) |  |  | U16 | 3,16 | 1 | 1
7318 | DAQ format |  |  | U16 | 3,16 | 1 | 1
7319 | DAQ device id |  |  | U16 | 3,16 | 1 | 1
7320 | DAQ bitspersample (0: 16bit, 1: 32bit) |  |  | U16 | 3,16 | 1 | 1
7321 | reserved |  |  | U16 | 3,16 | 1 | 9
PT #1~9
7330 | Frequency |  |  | U16 | 3,16 | 1 | 1
7331 | feeder count |  |  | U16 | 3,16 | 1 | 1
7332 | #1 wiring mode | 0: not used 1 : 3p4w 2 : 3p3w(2CT), 3 : 3p3w(3CT) 4: 1p2w(L1), 5 : 1p2w(L2), 6 : 1p2w(L3) 7: 1p3w, 8 : SIMULATION |  | U16 | 3,16 | 1 | 1
| #1 reserved |  |  | U16 | 3,16 | 1 | 1
7333 | #1 V nominal |  |  | U32 | 3,16 | 2 | 1
7335 | #1 PT1 |  |  | U32 | 3,16 | 2 | 1
7337 | #1 PT2 |  |  | U16 | 3,16 | 1 | 1
7338 | #1 reserved |  |  | U16 | 3,16 | 1 | 1
7339 | #2 PT |  |  | U16 | 3,16 | 1 | 8
7347 | #3 PT |  |  | U16 | 3,16 | 1 | 8
7355 | #4 PT |  |  | U16 | 3,16 | 1 | 8
7363 | #5 PT |  |  | U16 | 3,16 | 1 | 8
7371 | #6 PT |  |  | U16 | 3,16 | 1 | 8
7379 | #7 PT |  |  | U16 | 3,16 | 1 | 8
7387 | #8 PT |  |  | U16 | 3,16 | 1 | 8
7395 | #9 PT |  |  | U16 | 3,16 | 1 | 8
CT #1~9
7403 | #1 I Nominal |  |  | U16 | 3,16 | 1 | 1
7404 | #1 CT1 |  |  | U16 | 3,16 | 1 | 1
7405 | #1 CT2 | 0: 5A, 1: 100mA/333mV, 2: Rogowski |  | U16 | 3,16 | 1 | 1
7406 | #1 turns |  |  | U16 | 3,16 | 1 | 1
7407 | #1 Starting Current | (1.0 : 0.002*In, 0.5: 0.001*In) 0 ~ 10000 (단위 : mA) |  | U16 | 3,16 | 1 | 1
7408 | #1 CT1 direction | 0: positive, 1: negative |  | U16 | 3,16 | 1 | 1
7409 | #1 CT2 direction |  |  | U16 | 3,16 | 1 | 1
7410 | #1 CT3 direction |  |  | U16 | 3,16 | 1 | 1
7411 | #1 Rogowski CT Model |  |  | U16 | 3,16 | 1 | 1
7412 | #1 phase offset 1 | * phase resolution 60Hz: 0.0211, 50Hz: 0.0176 * range: +63 ~ -383 1.329 ~ -8.079 1.107 ~ -6.732 |  | U16 | 3,16 | 1 | 1
7413 | #1 phase offset 2 |  |  | U16 | 3,16 | 1 | 1
7414 | #1 phase offset 3 |  |  | U16 | 3,16 | 1 | 1
7415 | #1 ZCT Type | 1: 200mV:100mV 2: 200mV:1.5mA 3: 200mV:0.1mA |  | U16 | 3,16 | 1 | 1
7416 | #1 ZCT Scale |  |  | U16 | 3,16 | 1 | 1
7417 | #1 reserved |  |  | U16 | 3,16 | 1 | 2
7419 | #2 CT |  |  | U16 | 3,16 | 1 | 14
7433 | #3 CT |  |  | U16 | 3,16 | 1 | 14
7447 | #4 CT |  |  | U16 | 3,16 | 1 | 14
7461 | #5 CT |  |  | U16 | 3,16 | 1 | 14
7475 | #6 CT |  |  | U16 | 3,16 | 1 | 14
7489 | #7 CT |  |  | U16 | 3,16 | 1 | 14
7503 | #8 CT |  |  | U16 | 3,16 | 1 | 14
7517 | #9 CT |  |  | U16 | 3,16 | 1 | 14
ETC
7531 | VA type | 0: RMS(S=VA) 1: vector(S=sqrt(P*P+Q*Q) |  | U16 | 3,16 | 1 | 1
7532 | PF sign | 0: IEC, 1: IEEE |  | U16 | 3,16 | 1 | 1
7533 | demand interval |  |  | U16 | 3,16 | 1 | 1
7534 | Max. Demand for current TDD(A) - unused |  |  | U16 | 3,16 | 1 | 1
7535 | Target Demand (W) #1~6 |  |  | U32 | 3,16 | 2 | 6
7547 | backlight off time |  |  | U16 | 3,16 | 1 | 1
7548 | brightness |  |  | U16 | 3,16 | 1 | 1
7549 | auto rotation |  |  | U16 | 3,16 | 1 | 1
7550 | Time Zone (~720 ~ 720) | 분단위 |  | S16 | 3,16 | 1 | 1
7551 | max/min reset period | 0: daily 1: weekly 2: monthly |  | U16 | 3,16 | 1 | 1
7552 | TEST MODE | 0 : not use, 1 : use |  | U16 | 3,16 | 1 | 1
7553 | TEST MODE INTERVAL |  |  | U16 | 3,16 | 1 | 1
7554 |  |  |  | U16 |  | 1 | 2
IOM SETTING
7556 | type |  |  | U16 | 3,16 | 1 | 1
7557 | reserved |  |  | U16 | 3,16 | 1 | 3
7560 | DI TYPE #0~3 | 0 : DI, 1 : PI |  | U16 | 3,16 | 1 | 4
7564 | DI debounce #0~3 | 4~255ms |  | U16 | 3,16 | 1 | 4
7568 | PI Scale #0~3 |  |  | U16 | 3,16 | 1 | 4
7572 | reserved |  |  | U16 | 3,16 | 1 | 14
Command
7586 | UTC Time |  |  | U16 | 3,16 | 1 | 4
7590 |  |  |  | U16 | 3,16 | 1 | 6
7596 | reboot |  |  | U16 | 6 | 1 | 1
7597 | save settings |  |  | U16 | 6 | 1 | 1
7598 | Calibration command #1~9 | 0: Enable Calibration 1: U gain 2: I gain 3: W gain 4: Ph gain 5: clear V 6: clear I 7: clear W 8: clear phase 9: IN gain 10: clear IN 11: Disable Calibration 12: save Calibration 13: Upp gain 14: clear Upp gain 15: set dcos 16: clear DcOffset 17: --- 18: --- |  | U16 | 6 | 1 | 9
7607 | V-ref, 1=1V #1~9 |  |  | U16 | 6 | 1 | 9
7616 | I-ref, 1=0.1A #1~9 |  |  | U16 | 6 | 1 | 9
7625 | In-ref, 1=0.1 #1~9 |  |  | U16 | 6 | 1 | 9
7634 | init settings |  |  | U16 | 6 | 1 | 1
7635 | clear PI |  |  | U16 | 6 | 1 | 1
7636 | clear demand #1~9 |  |  | U16 | 6 | 1 | 9
7645 | clear minmax #1~9 |  |  | U16 | 6 | 1 | 9
7654 | clear energy #1~9 |  |  | U16 | 6 | 1 | 9
7663 | clear alarm #1~9 |  |  | U16 | 6 | 1 | 9
7672 | clear event #1~9 |  |  | U16 | 6 | 1 | 9
7681 | load event #1~9 | 1: down, 2:up, 3:top |  | U16 | 6 | 1 | 9
7690 | load alarm #1~9 | 1: down, 2:up, 3:top |  | U16 | 6 | 1 | 9
7699 | Alarm Ack #1~9 | not used |  | U16 | 6 | 1 | 9
7708 | Event Ack #1~9 | not used |  | U16 | 6 | 1 | 9
7717 | DAQ enable #1~9 |  |  | U16 | 6 | 1 | 9
7726 | load itic #1~3 | 1: down, 2:up, 3:top |  | U16 | 6 | 1 | 3
7729 | load itic2 #1~3 | 1: down, 2:up, 3:top |  | U16 | 6 | 1 | 3
7732 | clear ITIC #1~3 |  |  | U16 | 6 | 1 | 3
7735 | reserved |  |  | U16 | 6 | 1

## #2CH modbus
address | name | 설명 | Unit | TYPE | FC | Word Count | Item Count
Metering
10000 | Time Stamp |  |  | UTC | 3 | 2 | 1
10002 | TYPE |  |  | U16 | 3 | 1 | 1
10003 | STATUS | 1 : online, 0 : offline |  | U16 | 3 | 1 | 1
10004 | Frequency | 라인주파수 | Hz | float | 3 | 2 | 1
10006 | Internal Temp |  | ℃ | float | 3 | 2 | 1
10008 | U1 | 상전압 1 | V | float | 3 | 2 | 1
10010 | U2 | 상전압 2 |  | float | 3 | 2 | 1
10012 | U3 | 상전압 3 |  | float | 3 | 2 | 1
10014 | U~ | 상전압 평균 |  | float | 3 | 2 | 1
10016 | U12 | 선간 전압 12 |  | float | 3 | 2 | 1
10018 | U23 | 선간 전압 23 |  | float | 3 | 2 | 1
10020 | U31 | 선간 전압 31 |  | float | 3 | 2 | 1
10022 | Upp~ | 선간 전압 평균 |  | float | 3 | 2 | 1
10024 | Uunbalance2 |  | % | float | 3 | 2 | 1
10026 | Uunbalance0 |  |  | float | 3 | 2 | 1
10028 | U Zero Sequence Mag. |  |  | float | 3 | 2 | 1
10030 | U Zero Sequence angle |  |  | float | 3 | 2 | 1
10032 | U Positive Sequence Mag. |  |  | float | 3 | 2 | 1
10034 | U Positive Sequence angle |  |  | float | 3 | 2 | 1
10036 | U Negative Sequence Mag |  |  | float | 3 | 2 | 1
10038 | U Negative Sequence angle |  |  | float | 3 | 2 | 1
10040 | Angle U1 |  |  | float | 3 | 2 | 1
10042 | Angle U2 |  |  | float | 3 | 2 | 1
10044 | Angle U3 |  |  | float | 3 | 2 | 1
10046 | U Underdeviation L1 |  | % | float | 3 | 2 | 1
10048 | U Underdeviation L2 |  | % | float | 3 | 2 | 1
10050 | U Underdeviation L3 |  | % | float | 3 | 2 | 1
10052 | U Overdeviation L1 |  | % | float | 3 | 2 | 1
10054 | U Overdeviation L2 |  | % | float | 3 | 2 | 1
10056 | U Overdeviation L3 |  | % | float | 3 | 2 | 1
10058 | I1 | 상전류 1 | A | float | 3 | 2 | 1
10060 | I2 | 상전류 2 |  | float | 3 | 2 | 1
10062 | I3 | 상전류 3 |  | float | 3 | 2 | 1
10064 | I~ |  |  | float | 3 | 2 | 1
10066 | I total (I1+I2+I3) |  |  | float | 3 | 2 | 1
10068 | In(Measured) |  |  | float | 3 | 2 | 1
10070 | In(Calculated) | Ia+Ib+Ic+In = Ig |  | float | 3 | 2 | 1
10072 | Ig |  |  | float | 3 | 2 | 1
10074 | I Zero Sequence Mag |  |  | float | 3 | 2 | 1
10076 | I Zero Sequence angle |  |  | float | 3 | 2 | 1
10078 | I Positive Sequence Mag. |  |  | float | 3 | 2 | 1
10080 | I Positive Sequence angle |  |  | float | 3 | 2 | 1
10082 | I Negative Sequence Mag. |  |  | float | 3 | 2 | 1
10084 | I Negative Sequence angle |  |  | float | 3 | 2 | 1
10086 | Angle I1 |  |  | float | 3 | 2 | 1
10088 | Angle I2 |  |  | float | 3 | 2 | 1
10090 | Angle I3 |  |  | float | 3 | 2 | 1
10092 | Iunbalance2 |  | % | float | 3 | 2 | 1
10094 | Iunbalance0 |  |  | float | 3 | 2 | 1
10096 | P1 | 유효전력 P1 | W | float | 3 | 2 | 1
10098 | P2 | 유효전력 P2 |  | float | 3 | 2 | 1
10100 | P3 | 유효전력 P3 |  | float | 3 | 2 | 1
10102 | P total | 유효전력 P-total |  | float | 3 | 2 | 1
10104 | fP1 |  |  | float | 3 | 2 | 1
10106 | fP2 |  |  | float | 3 | 2 | 1
10108 | fP3 |  |  | float | 3 | 2 | 1
10110 | fP total |  |  | float | 3 | 2 | 1
10112 | Q1 | 무효전력 Q1 | VAR | float | 3 | 2 | 1
10114 | Q2 | 무효전력 Q2 |  | float | 3 | 2 | 1
10116 | Q3 | 무효전력 Q3 |  | float | 3 | 2 | 1
10118 | Q total | 무효전력 Q-total |  | float | 3 | 2 | 1
10120 | fQ1 |  |  | float | 3 | 2 | 1
10122 | fQ2 |  |  | float | 3 | 2 | 1
10124 | fQ3 |  |  | float | 3 | 2 | 1
10126 | fQ total |  |  | float | 3 | 2 | 1
10128 | S1 | 피상전력 S1 | VA | float | 3 | 2 | 1
10130 | S2 | 피상전력 S2 |  | float | 3 | 2 | 1
10132 | S3 | 피상전력 S3 |  | float | 3 | 2 | 1
10134 | S total | 피상전력 S-total |  | float | 3 | 2 | 1
10136 | fS1 |  |  | float | 3 | 2 | 1
10138 | fS2 |  |  | float | 3 | 2 | 1
10140 | fS3 |  |  | float | 3 | 2 | 1
10142 | fS total |  |  | float | 3 | 2 | 1
10144 | PF1 | 역률 PF1 | % | float | 3 | 2 | 1
10146 | PF2 | 역률 PF2 |  | float | 3 | 2 | 1
10148 | PF3 | 역률 PF3 |  | float | 3 | 2 | 1
10150 | PF total | 역률 PF-total |  | float | 3 | 2 | 1
10152 | dPF1 |  | % | float | 3 | 2 | 1
10154 | dPF2 |  |  | float | 3 | 2 | 1
10156 | dPF3 |  |  | float | 3 | 2 | 1
10158 | dPF total |  |  | float | 3 | 2 | 1
10160 | deformed Power D L1 |  | W | float | 3 | 2 | 1
10162 | deformed Power D L2 |  |  | float | 3 | 2 | 1
10164 | deformed Power D L3 |  |  | float | 3 | 2 | 1
10166 | deformed Power D Total |  |  | float | 3 | 2 | 1
10168 | Power Angle(atan(fPt,fQt) L1 |  | Degree | float | 3 | 2 | 1
10170 | Power Angle(atan(fPt,fQt) L2 |  |  | float | 3 | 2 | 1
10172 | Power Angle(atan(fPt,fQt) L3 |  |  | float | 3 | 2 | 1
10174 |  |  |  | float | 3 | 2 | 1
10176 | THD V1 |  | % | float | 3 | 2 | 1
10178 | THD V2 |  |  | float | 3 | 2 | 1
10180 | THD V3 |  |  | float | 3 | 2 | 1
10182 | THD V12 |  |  | float | 3 | 2 | 1
10184 | THD V23 |  |  | float | 3 | 2 | 1
10186 | THD V31 |  |  | float | 3 | 2 | 1
10188 | CF V1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
10190 | CF V2 |  |  | float | 3 | 2 | 1
10192 | CF V3 |  |  | float | 3 | 2 | 1
10194 | CF V12 |  |  | float | 3 | 2 | 1
10196 | CF V23 |  |  | float | 3 | 2 | 1
10198 | CF V31 |  |  | float | 3 | 2 | 1
10200 | THD I1 |  |  | float | 3 | 2 | 1
10202 | THD I2 |  |  | float | 3 | 2 | 1
10204 | THD I3 |  |  | float | 3 | 2 | 1
10206 | TDD I1 |  |  | float | 3 | 2 | 1
10208 | TDD I2 |  |  | float | 3 | 2 | 1
10210 | TDD I3 |  |  | float | 3 | 2 | 1
10212 | K I1 | K-FACTOR : 고조파 허용율 |  | float | 3 | 2 | 1
10214 | K I2 |  |  | float | 3 | 2 | 1
10216 | K I3 |  |  | float | 3 | 2 | 1
10218 | CF I1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
10220 | CF I2 |  |  | float | 3 | 2 | 1
10222 | CF I3 |  |  | float | 3 | 2 | 1
10224 | fU1 | 기본파 U1 | V | float | 3 | 2 | 1
10226 | fU2 | 기본파 U2 |  | float | 3 | 2 | 1
10228 | fU3 | 기본파 U3 |  | float | 3 | 2 | 1
10230 | fU~ | 기본파 전압 평균 |  | float | 3 | 2 | 1
10232 | fI1 | 기본파 I1 | A | float | 3 | 2 | 1
10234 | fI2 | 기본파 I2 |  | float | 3 | 2 | 1
10236 | fI3 | 기본파 I3 |  | float | 3 | 2 | 1
10238 | fI~ | 기본파 전류 평균 |  | float | 3 | 2 | 1
Energy
10240 | import kwh(0 ~ 999,999,999.9 kw) | 누적 유효전력량 |  | U32 | 3 | 2 | 1
10242 | export kwh |  |  | U32 | 3 | 2 | 1
10244 | import kvarh |  |  | U32 | 3 | 2 | 1
10246 | export kvarh |  |  | U32 | 3 | 2 | 1
10248 | kvah |  |  | U32 | 3 | 2 | 1
10250 |  |  |  | U32 | 3 | 2 | 1
10252 | import kwh this month |  |  | U32 | 3 | 2 | 1
10254 | export kwh this month |  |  | U32 | 3 | 2 | 1
10256 | import kvarh this month |  |  | U32 | 3 | 2 | 1
10258 | export kvarh this month |  |  | U32 | 3 | 2 | 1
10260 | kvah this month |  |  | U32 | 3 | 2 | 1
10262 |  |  |  | U32 | 3 | 2 | 1
10264 | import kwh last month |  |  | U32 | 3 | 2 | 1
10266 | export kwh last month |  |  | U32 | 3 | 2 | 1
10268 | import kvarh last month |  |  | U32 | 3 | 2 | 1
10270 | export kvarh last month |  |  | U32 | 3 | 2 | 1
10272 | kvah last month |  |  | U32 | 3 | 2 | 1
10274 |  |  |  | U32 | 3 | 2 | 1
10276 | import kwh | 0~999,999,999.999 kw |  | U64 | 3 | 4 | 1
10280 | export kwh |  |  | U64 | 3 | 4 | 1
10284 | import kvarh |  |  | U64 | 3 | 4 | 1
10288 | export kvarh |  |  | U64 | 3 | 4 | 1
10292 | kvah |  |  | U64 | 3 | 4 | 1
10296 |  |  |  | U64 | 3 | 4 | 1
Demand
10300 | Time Stamp |  |  | UTC | 3 | 2 | 1
10302 | Max Demand P(import) |  |  | float | 3 | 2 | 1
10304 | Time Stamp |  |  | UTC | 3 | 2 | 1
10306 | Max Demand P(export) |  |  | float | 3 | 2 | 1
10308 | Time Stamp |  |  | UTC | 3 | 2 | 1
10310 | Max Demand Q(import) |  |  | float | 3 | 2 | 1
10312 | Time Stamp |  |  | UTC | 3 | 2 | 1
10314 | Max Demand Q(export) |  |  | float | 3 | 2 | 1
10316 | Time Stamp |  |  | UTC | 3 | 2 | 1
10318 | Max Demand S |  |  | float | 3 | 2 | 1
10320 | Time Stamp |  |  | UTC | 3 | 2 | 1
10322 | Max Demand I1 |  |  | float | 3 | 2 | 1
10324 | Time Stamp |  |  | UTC | 3 | 2 | 1
10326 | Max Demand I2 |  |  | float | 3 | 2 | 1
10328 | Time Stamp |  |  | UTC | 3 | 2 | 1
10330 | Max Demand I3 |  |  | float | 3 | 2 | 1
10332 | Demand time stamp |  |  | UTC | 3 | 2 | 1
10334 | Demand P(import) |  |  | float | 3 | 2 | 1
10336 | Demand P(export) |  |  | float | 3 | 2 | 1
10338 | Demand Q(import) |  |  | float | 3 | 2 | 1
10340 | Demand Q(export) |  |  | float | 3 | 2 | 1
10342 | Demand S(export) |  |  | float | 3 | 2 | 1
10344 | Demand I1 |  |  | float | 3 | 2 | 1
10346 | Demand I2 |  |  | float | 3 | 2 | 1
10348 | Demand I3 |  |  | float | 3 | 2 | 1
10350 | Present Demand P(import) |  |  | float | 3 | 2 | 1
10352 | Present Demand P(export) |  |  | float | 3 | 2 | 1
10354 | Present Demand Q(import) |  |  | float | 3 | 2 | 1
10356 | Present Demand Q(export) |  |  | float | 3 | 2 | 1
10358 | Present Demand S(export) |  |  | float | 3 | 2 | 1
10360 | Forecast Demand P(export) |  |  | float | 3 | 2 | 1
10362 | Demand P 15m(import) |  |  | float | 3 | 2 | 1
10364 |  |  |  | float | 3 | 2 | 1
10366 |  |  |  | float | 3 | 2 | 1
10368 | Time Stamp(Demand Log 시작일) |  |  | U32 | 3 | 2 | 1
10370 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
10562 |  |  |  | float | 3 | 2 | 19
Voltage Quality RealTime Value
10600 | Voltage Under Deviation L1 |  | % | float | 3 | 2 | 1
10602 | Voltage Under Deviation L2 |  | % | float | 3 | 2 | 1
10604 | Voltage Under Deviation L3 |  | % | float | 3 | 2 | 1
10606 | Voltage Under Value L1 |  | rms | float | 3 | 2 | 1
10608 | Voltage Under Value L2 |  | rms | float | 3 | 2 | 1
10610 | Voltage Under Value L3 |  | rms | float | 3 | 2 | 1
10612 | Voltage Over Deviation L1 |  | % | float | 3 | 2 | 1
10614 | Voltage Over Deviation L2 |  | % | float | 3 | 2 | 1
10616 | Voltage Over Deviation L3 |  | % | float | 3 | 2 | 1
10618 | Voltage Over Value L1 |  | rms | float | 3 | 2 | 1
10620 | Voltage Over Value L2 |  | rms | float | 3 | 2 | 1
10622 | Voltage Over Value L3 |  | rms | float | 3 | 2 | 1
10624 | Flickers Pi L1 | 150/180 Cycles |  | float | 3 | 2 | 1
10626 | Flickers Pi L2 |  |  | float | 3 | 2 | 1
10628 | Flickers Pi L3 |  |  | float | 3 | 2 | 1
10630 | Flicker Pst L1 | 10min |  | float | 3 | 2 | 1
10632 | Flicker Pst L2 |  |  | float | 3 | 2 | 1
10634 | Flicker Pst L3 |  |  | float | 3 | 2 | 1
10636 | Flicker Plt L1 | 2hr |  | float | 3 | 2 | 1
10638 | Flicker Plt L2 |  |  | float | 3 | 2 | 1
10640 | Flicker Plt L3 |  |  | float | 3 | 2 | 1
10642 | Signaling Volt L1 | Magnitude of current 10/12 cycles as a percentage of nominal voltage. |  | float | 3 | 2 | 1
10644 | Signaling Volt L2 |  |  | float | 3 | 2 | 1
10646 | Signaling Volt L3 |  |  | float | 3 | 2 | 1
10648 | Signaling Volt Max L1 | Maximum magnitude of MSV from recording started as a percentage of nominal voltage |  | float | 3 | 2 | 1
10650 | Signaling Volt Max L2 |  |  | float | 3 | 2 | 1
10652 | Signaling Volt Max L3 |  |  | float | 3 | 2 | 1
10654 |  |  |  | float | 3 | 2 | 23
EN50160 This Week
10700 | start date |  |  | UTC | 3 | 2 | 1
10702 | end date |  |  | UTC | 3 | 2 | 1
10704 | status&compliance | bit 0: Freq Var1 bit 1: Freq Var2 bit 2: Volt Var1 L1 bit 3: Volt Var1 L2 bit 4: Volt Var1 L3 bit 5: Volt Var2 L1 bit 6: Volt Var2 L2 bit 7: Volt Var2 L3 bit 8: Unbalance bit 9: Volt THD L1 bit 10: Volt THD L2 bit 11: Volt THD L3 bit 12: Volt HD L1 bit 13: Volt HD L2 bit 14: Volt HD L3 bit 15: Pst L1 bit 16: Pst L2 bit 17: Pst L3 bit 18: Plt L1 bit 19: Plt L2 bit 20: Plt L3 bit 21: SigVolt L1 bit 22: SigVolt L2 bit 23: SigVolt L3 bit 31: Complete [status] 0: OK 1: failed |  | U32 | 3 | 2 | 1
10706 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1
10707 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1
10708 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
10709 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
10710 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1
10711 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
10712 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
10713 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1
10714 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
10715 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
10716 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1
10717 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
10718 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
10719 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1
10720 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
10721 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
10722 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1
10723 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
10724 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
10725 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1
10726 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
10727 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
10728 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1
10729 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
10730 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
10731 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1
10732 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
10733 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
10734 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
10735 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
10736 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
10737 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
10738 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
10739 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
10740 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
10741 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
10742 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
10743 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
10744 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
10745 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
10746 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
10747 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
10748 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
10749 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
EN50160 Last Week
10750 | start date |  |  | UTC | 3 | 2 | 1
10752 | end date |  |  | UTC | 3 | 2 | 1
10754 | status |  |  | U16 | 3 | 1 | 1
10755 | compilance |  |  | U16 | 3 | 1 | 1
10756 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1
10757 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1
10758 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
10759 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
10760 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1
10761 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
10762 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
10763 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1
10764 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
10765 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
10766 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1
10767 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
10768 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
10769 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1
10770 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
10771 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
10772 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1
10773 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
10774 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
10775 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1
10776 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
10777 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
10778 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1
10779 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
10780 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
10781 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1
10782 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
10783 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
10784 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
10785 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
10786 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
10787 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
10788 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
10789 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
10790 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
10791 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
10792 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
10793 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
10794 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
10795 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
10796 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
10797 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
10798 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
10799 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
Harmonics
10800 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
10864 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
10928 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
10992 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
11056 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
11120 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
11184 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
11248 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
11312 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
11376 |  |  |  | S16 | 3 | 1 | 24
Inter Harmonics
11400 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
11464 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
11528 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
11592 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
11656 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
11720 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
11784 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
11848 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
11912 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
11976 |  |  |  | S16 | 3 | 1 | 24
Max/Min
12000 | fr |  |  | U16 | 3 | 1 | 1
12001 | re |  |  | U16 | 3 | 1 | 1
12002 | Reset TimeStamp |  |  | UTC | 3 | 2 | 1
12004 | Frequency |  |  | float | 3 | 2 | 4
12012 | Temp |  |  | float | 3 | 2 | 4
12020 | U1 |  |  | float | 3 | 2 | 4
12028 | U2 |  |  | float | 3 | 2 | 4
12036 | U3 |  |  | float | 3 | 2 | 4
12044 | U~ |  |  | float | 3 | 2 | 4
12052 | U12 |  |  | float | 3 | 2 | 4
12060 | U23 |  |  | float | 3 | 2 | 4
12068 | U31 |  |  | float | 3 | 2 | 4
12076 | Upp~ |  |  | float | 3 | 2 | 4
12084 | I1 |  |  | float | 3 | 2 | 4
12092 | I2 |  |  | float | 3 | 2 | 4
12100 | I3 |  |  | float | 3 | 2 | 4
12108 | I~ |  |  | float | 3 | 2 | 4
12116 | I total |  |  | float | 3 | 2 | 4
12124 | In |  |  | float | 3 | 2 | 4
12132 | Isum |  |  | float | 3 | 2 | 4
12140 | P1 |  |  | float | 3 | 2 | 4
12148 | P2 |  |  | float | 3 | 2 | 4
12156 | P3 |  |  | float | 3 | 2 | 4
12164 | P total |  |  | float | 3 | 2 | 4
12172 | Q1 |  |  | float | 3 | 2 | 4
12180 | Q2 |  |  | float | 3 | 2 | 4
12188 | Q3 |  |  | float | 3 | 2 | 4
12196 | Q total |  |  | float | 3 | 2 | 4
12204 | S1 |  |  | float | 3 | 2 | 4
12212 | S2 |  |  | float | 3 | 2 | 4
12220 | S3 |  |  | float | 3 | 2 | 4
12228 | S total |  |  | float | 3 | 2 | 4
12236 | PF L1 |  |  | float | 3 | 2 | 4
12244 | PF L2 |  |  | float | 3 | 2 | 4
12252 | PF L3 |  |  | float | 3 | 2 | 4
12260 | PF total |  |  | float | 3 | 2 | 4
12268 | THD U1 |  |  | float | 3 | 2 | 4
12276 | THD U2 |  |  | float | 3 | 2 | 4
12284 | THD U3 |  |  | float | 3 | 2 | 4
12292 | THD U12 |  |  | float | 3 | 2 | 4
12300 | THD U23 |  |  | float | 3 | 2 | 4
12308 | THD U31 |  |  | float | 3 | 2 | 4
12316 | THD I1 |  |  | float | 3 | 2 | 4
12324 | THD I2 |  |  | float | 3 | 2 | 4
12332 | THD I3 |  |  | float | 3 | 2 | 4
12340 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
12342 | reserved |  |  | U16 | 3 | 1 | 1
12343 | CRC |  |  | U16 | 3 | 1 | 1
12344 |  |  |  | U16 | 3 | 1 | 6
alarm status
12350 | fr |  |  | U16 | 3 | 1 | 1
12351 | re |  |  | U16 | 3 | 1 | 1
12352 | reset Ts |  |  | UTC | 3 | 2 | 1
12354 | Alarm State #1 | Alarm Channel |  | U16 | 3 | 1 | 1
12355 |  | Alarm Condition |  | U16 | 3 | 1 | 1
12356 |  | Alarm Level |  | float | 3 | 2 | 1
12358 |  | Alarm Status |  | U16 | 3 | 1 | 1
12359 |  | Alarm Count |  | U16 | 3 | 1 | 1
12360 | Alarm State #2 |  |  | U16 | 3 | 1 | 6
12366 | Alarm State #3 |  |  | U16 | 3 | 1 | 6
12372 | Alarm State #4 |  |  | U16 | 3 | 1 | 6
12378 | Alarm State #5 |  |  | U16 | 3 | 1 | 6
12384 | Alarm State #6 |  |  | U16 | 3 | 1 | 6
12390 | Alarm State #7 |  |  | U16 | 3 | 1 | 6
12396 | Alarm State #8 |  |  | U16 | 3 | 1 | 6
12402 | Alarm State #9 |  |  | U16 | 3 | 1 | 6
12408 | Alarm State #10 |  |  | U16 | 3 | 1 | 6
12414 | Alarm State #11 |  |  | U16 | 3 | 1 | 6
12420 | Alarm State #12 |  |  | U16 | 3 | 1 | 6
12426 | Alarm State #13 |  |  | U16 | 3 | 1 | 6
12432 | Alarm State #14 |  |  | U16 | 3 | 1 | 6
12438 | Alarm State #15 |  |  | U16 | 3 | 1 | 6
12444 | Alarm State #16 |  |  | U16 | 3 | 1 | 6
12450 | Alarm State #17 |  |  | U16 | 3 | 1 | 6
12456 | Alarm State #18 |  |  | U16 | 3 | 1 | 6
12462 | Alarm State #19 |  |  | U16 | 3 | 1 | 6
12468 | Alarm State #20 |  |  | U16 | 3 | 1 | 6
12474 | Alarm State #21 |  |  | U16 | 3 | 1 | 6
12480 | Alarm State #22 |  |  | U16 | 3 | 1 | 6
12486 | Alarm State #23 |  |  | U16 | 3 | 1 | 6
12492 | Alarm State #24 |  |  | U16 | 3 | 1 | 6
12498 | Alarm State #25 |  |  | U16 | 3 | 1 | 6
12504 | Alarm State #26 |  |  | U16 | 3 | 1 | 6
12510 | Alarm State #27 |  |  | U16 | 3 | 1 | 6
12516 | Alarm State #28 |  |  | U16 | 3 | 1 | 6
12522 | Alarm State #29 |  |  | U16 | 3 | 1 | 6
12528 | Alarm State #30 |  |  | U16 | 3 | 1 | 6
12534 | Alarm State #31 |  |  | U16 | 3 | 1 | 6
12540 | Alarm State #32 |  |  | U16 | 3 | 1 | 6
12546 | update Ts |  |  | U32 | 3 | 2 | 1
12548 | Global Alarm Status | (alarm 하나라도 있으면 1, 아니면 0) |  | U16 | 3 | 1 | 1
12549 |  |  |  | U16 | 3 | 1 | 1
alarm log
12550 | fr | 0 ~ 1023 |  | U16 | 3 | 1 | 1
12551 | re | 0 ~ 1023 |  | U16 | 3 | 1 | 1
12552 | count | 전체 log 수 |  | U16 | 3 | 1 | 1
12553 | seq |  |  | U16 | 3 | 1 | 1
12554 | Alarm Log #1 | Time Stamp |  | UTC | 3 | 2 | 1
12556 |  | status |  | U16 | 3 | 1 | 1
12557 |  | Alarm Channel & Condition |  | U16 | 3 | 1 | 1
12558 |  | level |  | float | 3 | 2 | 1
12560 |  | Value |  | float | 3 | 2 | 1
12562 | Alarm Log #2 |  |  | U16 | 3 | 1 | 8
12570 | Alarm Log #3 |  |  | U16 | 3 | 1 | 8
12578 | Alarm Log #4 |  |  | U16 | 3 | 1 | 8
12586 | Alarm Log #5 |  |  | U16 | 3 | 1 | 8
12594 | Alarm Log #6 |  |  | U16 | 3 | 1 | 8
12602 | Alarm Log #7 |  |  | U16 | 3 | 1 | 8
12610 | Alarm Log #8 |  |  | U16 | 3 | 1 | 8
12618 | Alarm Log #9 |  |  | U16 | 3 | 1 | 8
12626 | Alarm Log #10 |  |  | U16 | 3 | 1 | 8
12634 | Alarm Log #11 |  |  | U16 | 3 | 1 | 8
12642 | Alarm Log #12 |  |  | U16 | 3 | 1 | 8
12650 | Alarm Log #13 |  |  | U16 | 3 | 1 | 8
12658 | Alarm Log #14 |  |  | U16 | 3 | 1 | 8
12666 | Alarm Log #15 |  |  | U16 | 3 | 1 | 8
12674 | Alarm Log #16 |  |  | U16 | 3 | 1 | 8
12682 | Alarm Log #17 |  |  | U16 | 3 | 1 | 8
12690 | Alarm Log #18 |  |  | U16 | 3 | 1 | 8
12698 | Alarm Log #19 |  |  | U16 | 3 | 1 | 8
12706 | Alarm Log #20 |  |  | U16 | 3 | 1 | 8
12714 | Alarm Log #21 |  |  | U16 | 3 | 1 | 8
12722 | Alarm Log #22 |  |  | U16 | 3 | 1 | 8
12730 | Alarm Log #23 |  |  | U16 | 3 | 1 | 8
12738 | Alarm Log #24 |  |  | U16 | 3 | 1 | 8
12746 | Alarm Log #25 |  |  | U16 | 3 | 1 | 8
12754 | Alarm Log #26 |  |  | U16 | 3 | 1 | 8
12762 | Alarm Log #27 |  |  | U16 | 3 | 1 | 8
12770 | Alarm Log #28 |  |  | U16 | 3 | 1 | 8
12778 | Alarm Log #29 |  |  | U16 | 3 | 1 | 8
12786 | Alarm Log #30 |  |  | U16 | 3 | 1 | 8
12794 | Alarm Log #31 |  |  | U16 | 3 | 1 | 8
12802 | Alarm Log #32 |  |  | U16 | 3 | 1 | 8
12810 |  |  |  | U16 | 3 | 1 | 40
이벤트 리스트
12850 | fr | 0 ~ 1023 |  | U16 | 3 | 1 | 1
12851 | re | 0 ~ 1023 |  | U16 | 3 | 1 | 1
12852 | count | 0 ~ 1023 |  | U16 | 3 | 1 | 1
12853 | seq |  |  | U16 | 3 | 1 | 1
PQ 이벤트(Sag, Swell, Transient, OC)
12854 | start ts |  |  | UTC | 3 | 2 | 1
12856 | start ts(ms) |  |  | U16 | 3 | 1 | 1
12857 | duration |  |  | U16 | 3 | 1 | 1
12858 | type | 1 : E_SAG 2 : E_SWELL 3 : E_sINTR 4 : E_lINTR 5 : E_OC 6 : E_RVC 7 : E_TrV 8 : E_TrC |  | U16 | 3 | 1 | 1
12859 | mask |  |  | U16 | 3 | 1 | 1
12860 | Level 1 |  |  | float | 3 | 2 | 1
12862 | Level 2 |  |  | float | 3 | 2 | 1
12864 | Level 3 |  |  | float | 3 | 2 | 1
12866 | PQ Event #2 |  |  | U16 | 3 | 1 | 12
12878 | PQ Event #3 |  |  | U16 | 3 | 1 | 12
12890 | PQ Event #4 |  |  | U16 | 3 | 1 | 12
12902 | PQ Event #5 |  |  | U16 | 3 | 1 | 12
12914 | PQ Event #6 |  |  | U16 | 3 | 1 | 12
12926 | PQ Event #7 |  |  | U16 | 3 | 1 | 12
12938 | PQ Event #8 |  |  | U16 | 3 | 1 | 12
12950 | PQ Event #9 |  |  | U16 | 3 | 1 | 12
12962 | PQ Event #10 |  |  | U16 | 3 | 1 | 12
12974 | PQ Event #11 |  |  | U16 | 3 | 1 | 12
12986 | PQ Event #12 |  |  | U16 | 3 | 1 | 12
12998 | PQ Event #13 |  |  | U16 | 3 | 1 | 12
13010 | PQ Event #14 |  |  | U16 | 3 | 1 | 12
13022 | PQ Event #15 |  |  | U16 | 3 | 1 | 12
13034 | PQ Event #16 |  |  | U16 | 3 | 1 | 12
13046 | PQ Event #17 |  |  | U16 | 3 | 1 | 12
13058 | PQ Event #18 |  |  | U16 | 3 | 1 | 12
13070 | PQ Event #19 |  |  | U16 | 3 | 1 | 12
13082 | PQ Event #20 |  |  | U16 | 3 | 1 | 12
13094 | PQ Event #21 |  |  | U16 | 3 | 1 | 12
13106 | PQ Event #22 |  |  | U16 | 3 | 1 | 12
13118 | PQ Event #23 |  |  | U16 | 3 | 1 | 12
13130 | PQ Event #24 |  |  | U16 | 3 | 1 | 12
13142 | PQ Event #25 |  |  | U16 | 3 | 1 | 12
13154 | PQ Event #26 |  |  | U16 | 3 | 1 | 12
13166 | PQ Event #27 |  |  | U16 | 3 | 1 | 12
13178 | PQ Event #28 |  |  | U16 | 3 | 1 | 12
13190 | PQ Event #29 |  |  | U16 | 3 | 1 | 12
13202 | PQ Event #30 |  |  | U16 | 3 | 1 | 12
13214 | PQ Event #31 |  |  | U16 | 3 | 1 | 12
13226 | PQ Event #32 |  |  | U16 | 3 | 1 | 12
13238 |  |  |  | U16 | 3 | 1 | 2
PQ Event Counter
13240 |  |  |  | U16 | 3 | 1 | 1
13241 |  |  |  | U16 | 3 | 1 | 1
13242 |  |  |  | U16 | 3 | 1 | 1
13243 | Sag Coount |  |  | U16 | 3 | 1 | 1
13244 | Swell Count |  |  | U16 | 3 | 1 | 1
13245 |  |  |  | U16 | 3 | 1 | 1
13246 |  |  |  | U16 | 3 | 1 | 1
13247 |  |  |  | U16 | 3 | 1 | 1
13248 |  |  |  | U16 | 3 | 1 | 1
13249 |  |  |  | U16 | 3 | 1 | 1
Wave Sample
13250 | Wave Form V1 (160 sample) |  |  | S16 | 3 | 1 | 160
13410 | Wave Form V2 (160 sample) |  |  | S16 | 3 | 1 | 160
13570 | Wave Form V3 (160 sample) |  |  | S16 | 3 | 1 | 160
13730 | Wave Form V12 (160 sample) |  |  | S16 | 3 | 1 | 160
13890 | Wave Form V23 (160 sample) |  |  | S16 | 3 | 1 | 160
14050 | Wave Form V31 (160 sample) |  |  | S16 | 3 | 1 | 160
14210 | Wave Form I1 (160 sample) |  |  | S16 | 3 | 1 | 160
14370 | Wave Form I2 (160 sample) |  |  | S16 | 3 | 1 | 160
14530 | Wave Form I3 (160 sample) |  |  | S16 | 3 | 1 | 160
14690 | vscale |  |  | float | 3 | 2 | 1
14692 | iscale |  |  | float | 3 | 2 | 1
14694 |  |  |  | S16 | 3 | 1 | 6
월간리포트 생성위한 10분 평균
14700 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
14702 | U1 |  |  | float | 3 | 2 | 1
14704 | U2 |  |  | float | 3 | 2 | 1
14706 | U3 |  |  | float | 3 | 2 | 1
14708 | U THD1 |  |  | float | 3 | 2 | 1
14710 | U THD2 |  |  | float | 3 | 2 | 1
14712 | U THD3 |  |  | float | 3 | 2 | 1
14714 | Upp THD1 |  |  | float | 3 | 2 | 1
14716 | Upp THD2 |  |  | float | 3 | 2 | 1
14718 | Upp THD3 |  |  | float | 3 | 2 | 1
14720 | U Unbal Uu |  |  | float | 3 | 2 | 1
14722 | U Unbal Uo |  |  | float | 3 | 2 | 1
14724 | I1 |  |  | float | 3 | 2 | 1
14726 | I2 |  |  | float | 3 | 2 | 1
14728 | I3 |  |  | float | 3 | 2 | 1
14730 | In |  |  | float | 3 | 2 | 1
14732 | I THD1 |  |  | float | 3 | 2 | 1
14734 | I THD2 |  |  | float | 3 | 2 | 1
14736 | I THD3 |  |  | float | 3 | 2 | 1
14738 | I TDD1 |  |  | float | 3 | 2 | 1
14740 | I TDD2 |  |  | float | 3 | 2 | 1
14742 | I TDD3 |  |  | float | 3 | 2 | 1
14744 | K-factor 1 |  |  | float | 3 | 2 | 1
14746 | K-factor 2 |  |  | float | 3 | 2 | 1
14748 | K-factor 3 |  |  | float | 3 | 2 | 1
14750 | I Unbal Iu |  |  | float | 3 | 2 | 1
14752 | I Unbal Io |  |  | float | 3 | 2 | 1
14754 | kw imp |  |  | float | 3 | 2 | 1
14756 | kw exp |  |  | float | 3 | 2 | 1
14758 | kvar lag |  |  | float | 3 | 2 | 1
14760 | kvar lead |  |  | float | 3 | 2 | 1
14762 | kVA |  |  | float | 3 | 2 | 1
14764 | PF |  |  | float | 3 | 2 | 1
14766 | dPF |  |  | float | 3 | 2 | 1
14768 | temperature #1 |  |  | float | 3 | 2 | 1
14770 | temperature #2 |  |  | float | 3 | 2 | 1
14772 | temperature #3 |  |  | float | 3 | 2 | 1
14774 | temperature #4 |  |  | float | 3 | 2 | 1
14776 | temperature #5 |  |  | float | 3 | 2 | 1
14778 | Harmonics V1 |  |  | S16 | 3 | 1 | 24
14802 | Harmonics V2 |  |  | S16 | 3 | 1 | 24
14826 | Harmonics V3 |  |  | S16 | 3 | 1 | 24
14850 | Harmonics V12 |  |  | S16 | 3 | 1 | 24
14874 | Harmonics V23 |  |  | S16 | 3 | 1 | 24
14898 | Harmonics V31 |  |  | S16 | 3 | 1 | 24
14922 | Harmonics I1 |  |  | S16 | 3 | 1 | 24
14946 | Harmonics I2 |  |  | S16 | 3 | 1 | 24
14970 | Harmonics I3 |  |  | S16 | 3 | 1 | 24
14994 |  |  |  | U16 | 3 | 1 | 6
Energy log
15000 | Time Stamp |  |  | UTC | 3 | 2 | 1
15002 | kwh import |  |  | float | 3 | 2 | 1
15004 | kvarh lag |  |  | float | 3 | 2 | 1
15006 | kvarh lead |  |  | float | 3 | 2 | 1
15008 | kVAh |  |  | float | 3 | 2 | 1
15010 | energy log last day 01h |  |  | float | 3 | 2 | 4
15018 | energy log last day 02h |  |  | float | 3 | 2 | 4
15026 | energy log last day 03h |  |  | float | 3 | 2 | 4
15034 | energy log last day 04h |  |  | float | 3 | 2 | 4
15042 | energy log last day 05h |  |  | float | 3 | 2 | 4
15050 | energy log last day 06h |  |  | float | 3 | 2 | 4
15058 | energy log last day 07h |  |  | float | 3 | 2 | 4
15066 | energy log last day 08h |  |  | float | 3 | 2 | 4
15074 | energy log last day 09h |  |  | float | 3 | 2 | 4
15082 | energy log last day 10h |  |  | float | 3 | 2 | 4
15090 | energy log last day 11h |  |  | float | 3 | 2 | 4
15098 | energy log last day 12h |  |  | float | 3 | 2 | 4
15106 | energy log last day 13h |  |  | float | 3 | 2 | 4
15114 | energy log last day 14h |  |  | float | 3 | 2 | 4
15122 | energy log last day 15h |  |  | float | 3 | 2 | 4
15130 | energy log last day 16h |  |  | float | 3 | 2 | 4
15138 | energy log last day 17h |  |  | float | 3 | 2 | 4
15146 | energy log last day 18h |  |  | float | 3 | 2 | 4
15154 | energy log last day 19h |  |  | float | 3 | 2 | 4
15162 | energy log last day 20h |  |  | float | 3 | 2 | 4
15170 | energy log last day 21h |  |  | float | 3 | 2 | 4
15178 | energy log last day 22h |  |  | float | 3 | 2 | 4
15186 | energy log last day 23h |  |  | float | 3 | 2 | 4
15194 |  |  |  | U16 | 3 | 1 | 6
15200 | Time Stamp |  |  | UTC | 3 | 2 | 1
15202 | kwh import |  |  | float | 3 | 2 | 1
15204 | kvarh lag |  |  | float | 3 | 2 | 1
15206 | kvarh lead |  |  | float | 3 | 2 | 1
15208 | kVAh |  |  | float | 3 | 2 | 1
15210 | energy log this day 01h |  |  | float | 3 | 2 | 4
15218 | energy log this day 02h |  |  | float | 3 | 2 | 4
15226 | energy log this day 03h |  |  | float | 3 | 2 | 4
15234 | energy log this day 04h |  |  | float | 3 | 2 | 4
15242 | energy log this day 05h |  |  | float | 3 | 2 | 4
15250 | energy log this day 06h |  |  | float | 3 | 2 | 4
15258 | energy log this day 07h |  |  | float | 3 | 2 | 4
15266 | energy log this day 08h |  |  | float | 3 | 2 | 4
15274 | energy log this day 09h |  |  | float | 3 | 2 | 4
15282 | energy log this day 10h |  |  | float | 3 | 2 | 4
15290 | energy log this day 11h |  |  | float | 3 | 2 | 4
15298 | energy log this day 12h |  |  | float | 3 | 2 | 4
15306 | energy log this day 13h |  |  | float | 3 | 2 | 4
15314 | energy log this day 14h |  |  | float | 3 | 2 | 4
15322 | energy log this day 15h |  |  | float | 3 | 2 | 4
15330 | energy log this day 16h |  |  | float | 3 | 2 | 4
15338 | energy log this day 17h |  |  | float | 3 | 2 | 4
15346 | energy log this day 18h |  |  | float | 3 | 2 | 4
15354 | energy log this day 19h |  |  | float | 3 | 2 | 4
15362 | energy log this day 20h |  |  | float | 3 | 2 | 4
15370 | energy log this day 21h |  |  | float | 3 | 2 | 4
15378 | energy log this day 22h |  |  | float | 3 | 2 | 4
15386 | energy log this day 23h |  |  | float | 3 | 2 | 4
15394 |  |  |  | U16 | 3 | 1 | 6
demand log last day
15400 | Time Stamp |  |  | U32 | 3 | 2 | 1
15402 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
15594 |  |  |  | U16 | 3 | 1 | 6
Max/Min last data
15600 | fr |  |  | S16 | 3 | 1 | 1
15601 | re |  |  | S16 | 3 | 1 | 1
15602 | Reset TimeStamp |  |  | UTC | 3 | 2 | 1
15604 | Frequency |  |  | float | 3 | 2 | 4
15612 | Temp |  |  | float | 3 | 2 | 4
15620 | U1 |  |  | float | 3 | 2 | 4
15628 | U2 |  |  | float | 3 | 2 | 4
15636 | U3 |  |  | float | 3 | 2 | 4
15644 | U~ |  |  | float | 3 | 2 | 4
15652 | U12 |  |  | float | 3 | 2 | 4
15660 | U23 |  |  | float | 3 | 2 | 4
15668 | U31 |  |  | float | 3 | 2 | 4
15676 | Upp~ |  |  | float | 3 | 2 | 4
15684 | I1 |  |  | float | 3 | 2 | 4
15692 | I2 |  |  | float | 3 | 2 | 4
15700 | I3 |  |  | float | 3 | 2 | 4
15708 | I~ |  |  | float | 3 | 2 | 4
15716 | I total |  |  | float | 3 | 2 | 4
15724 | In |  |  | float | 3 | 2 | 4
15732 | Isum |  |  | float | 3 | 2 | 4
15740 | P1 |  |  | float | 3 | 2 | 4
15748 | P2 |  |  | float | 3 | 2 | 4
15756 | P3 |  |  | float | 3 | 2 | 4
15764 | P total |  |  | float | 3 | 2 | 4
15772 | Q1 |  |  | float | 3 | 2 | 4
15780 | Q2 |  |  | float | 3 | 2 | 4
15788 | Q3 |  |  | float | 3 | 2 | 4
15796 | Q total |  |  | float | 3 | 2 | 4
15804 | S1 |  |  | float | 3 | 2 | 4
15812 | S2 |  |  | float | 3 | 2 | 4
15820 | S3 |  |  | float | 3 | 2 | 4
15828 | S total |  |  | float | 3 | 2 | 4
15836 | PF L1 |  |  | float | 3 | 2 | 4
15844 | PF L2 |  |  | float | 3 | 2 | 4
15852 | PF L3 |  |  | float | 3 | 2 | 4
15860 | PF total |  |  | float | 3 | 2 | 4
15868 | THD U1 |  |  | float | 3 | 2 | 4
15876 | THD U2 |  |  | float | 3 | 2 | 4
15884 | THD U3 |  |  | float | 3 | 2 | 4
15892 | THD U12 |  |  | float | 3 | 2 | 4
15900 | THD U23 |  |  | float | 3 | 2 | 4
15908 | THD U31 |  |  | float | 3 | 2 | 4
15916 | THD I1 |  |  | float | 3 | 2 | 4
15924 | THD I2 |  |  | float | 3 | 2 | 4
15932 | THD I3 |  |  | float | 3 | 2 | 4
15940 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
15942 | reserved |  |  | U16 | 3 | 1 | 1
15943 | CRC |  |  | U16 | 3 | 1 | 1
15944 |  |  |  | U16 | 3 | 1 | 6
ITIC
15950 | fr |  |  | U16 | 3 | 1 | 1
15951 | re |  |  | U16 | 3 | 1 | 1
15952 | count |  |  | U16 | 3 | 1 | 1
15953 | SEQ |  |  | U16 | 3 | 1 | 1
15954 | Log #1 | start ts |  | UTC | 3 | 2 | 1
15956 |  | start ts(ms) |  | U16 | 3 | 1 | 1
15957 |  | duration |  | U16 | 3 | 1 | 1
15958 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
15959 |  | mask |  | U16 | 3 | 1 | 1
15960 |  | Level 1 |  | float | 3 | 2 | 1
15962 |  | Level 2 |  | float | 3 | 2 | 1
15964 |  | Level 3 |  | float | 3 | 2 | 1
15966 |  | Normal |  | float | 3 | 2 | 1
15968 | Log #2 |  |  | U16 | 3 | 1 | 14
15982 | Log #3 |  |  | U16 | 3 | 1 | 14
15996 | Log #4 |  |  | U16 | 3 | 1 | 14
16010 | Log #5 |  |  | U16 | 3 | 1 | 14
16024 | Log #6 |  |  | U16 | 3 | 1 | 14
16038 | Log #7 |  |  | U16 | 3 | 1 | 14
16052 | Log #8 |  |  | U16 | 3 | 1 | 14
16066 | Log #9 |  |  | U16 | 3 | 1 | 14
16080 | Log #10 |  |  | U16 | 3 | 1 | 14
16094 | Log #11 |  |  | U16 | 3 | 1 | 14
16108 | Log #12 |  |  | U16 | 3 | 1 | 14
16122 | Log #13 |  |  | U16 | 3 | 1 | 14
16136 | Log #14 |  |  | U16 | 3 | 1 | 14
16150 | Log #15 |  |  | U16 | 3 | 1 | 14
16164 | Log #16 |  |  | U16 | 3 | 1 | 14
16178 | Log #17 |  |  | U16 | 3 | 1 | 14
16192 | Log #18 |  |  | U16 | 3 | 1 | 14
16206 | Log #19 |  |  | U16 | 3 | 1 | 14
16220 | Log #20 |  |  | U16 | 3 | 1 | 14
16234 | Log #21 |  |  | U16 | 3 | 1 | 14
16248 | Log #22 |  |  | U16 | 3 | 1 | 14
16262 | Log #23 |  |  | U16 | 3 | 1 | 14
16276 | Log #24 |  |  | U16 | 3 | 1 | 14
16290 | Log #25 |  |  | U16 | 3 | 1 | 14
16304 | Log #26 |  |  | U16 | 3 | 1 | 14
16318 | Log #27 |  |  | U16 | 3 | 1 | 14
16332 | Log #28 |  |  | U16 | 3 | 1 | 14
16346 | Log #29 |  |  | U16 | 3 | 1 | 14
16360 | Log #30 |  |  | U16 | 3 | 1 | 14
16374 | Log #31 |  |  | U16 | 3 | 1 | 14
16388 | Log #32 |  |  | U16 | 3 | 1 | 14
16402 |  |  |  | U16 | 3 | 1 | 8
ITIC(Configurator)
16410 | fr |  |  | U16 | 3 | 1 | 1
16411 | re |  |  | U16 | 3 | 1 | 1
16412 | count |  |  | U16 | 3 | 1 | 1
16413 | reserved |  |  | U16 | 3 | 1 | 1
16414 | Log #1 | start ts |  | UTC | 3 | 2 | 1
16416 |  | start ts(ms) |  | U16 | 3 | 1 | 1
16417 |  | duration |  | U16 | 3 | 1 | 1
16418 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
16419 |  | mask |  | U16 | 3 | 1 | 1
16420 |  | Level 1 |  | float | 3 | 2 | 1
16422 |  | Level 2 |  | float | 3 | 2 | 1
16424 |  | Level 3 |  | float | 3 | 2 | 1
16426 |  | Normal |  | float | 3 | 2 | 1
16428 | Log #2 |  |  | U16 | 3 | 1 | 14
16442 | Log #3 |  |  | U16 | 3 | 1 | 14
16456 | Log #4 |  |  | U16 | 3 | 1 | 14
16470 | Log #5 |  |  | U16 | 3 | 1 | 14
16484 | Log #6 |  |  | U16 | 3 | 1 | 14
16498 | Log #7 |  |  | U16 | 3 | 1 | 14
16512 | Log #8 |  |  | U16 | 3 | 1 | 14
16526 | Log #9 |  |  | U16 | 3 | 1 | 14
16540 | Log #10 |  |  | U16 | 3 | 1 | 14
16554 | Log #11 |  |  | U16 | 3 | 1 | 14
16568 | Log #12 |  |  | U16 | 3 | 1 | 14
16582 | Log #13 |  |  | U16 | 3 | 1 | 14
16596 | Log #14 |  |  | U16 | 3 | 1 | 14
16610 | Log #15 |  |  | U16 | 3 | 1 | 14
16624 | Log #16 |  |  | U16 | 3 | 1 | 14
16638 | Log #17 |  |  | U16 | 3 | 1 | 14
16652 | Log #18 |  |  | U16 | 3 | 1 | 14
16666 | Log #19 |  |  | U16 | 3 | 1 | 14
16680 | Log #20 |  |  | U16 | 3 | 1 | 14
16694 | Log #21 |  |  | U16 | 3 | 1 | 14
16708 | Log #22 |  |  | U16 | 3 | 1 | 14
16722 | Log #23 |  |  | U16 | 3 | 1 | 14
16736 | Log #24 |  |  | U16 | 3 | 1 | 14
16750 | Log #25 |  |  | U16 | 3 | 1 | 14
16764 | Log #26 |  |  | U16 | 3 | 1 | 14
16778 | Log #27 |  |  | U16 | 3 | 1 | 14
16792 | Log #28 |  |  | U16 | 3 | 1 | 14
16806 | Log #29 |  |  | U16 | 3 | 1 | 14
16820 | Log #30 |  |  | U16 | 3 | 1 | 14
16834 | Log #31 |  |  | U16 | 3 | 1 | 14
16848 | Log #32 |  |  | U16 | 3 | 1 | 14
16862 |  |  |  | U16 | 3 | 1 | 8
Setting 영역 시작
PQ Event
16870 | OC Level | 정격의 2배 |  | U16 | 3,16 | 1 | 1
16871 | OC Cycle | unused |  | U16 | 3,16 | 1 | 1
16872 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
16873 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
16874 |  |  |  | U16 | 3,16 | 1 | 2
16876 | Sag Level(%), 90% | < 90% |  | U16 | 3,16 | 1 | 1
16877 | Sag Cycle | unused |  | U16 | 3,16 | 1 | 1
16878 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
16879 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
16880 |  |  |  | U16 | 3,16 | 1 | 2
16882 | Swell Level(%), 110~200~ | > 110% |  | U16 | 3,16 | 1 | 1
16883 | Swell Cycle | unused |  | U16 | 3,16 | 1 | 1
16884 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
16885 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
16886 |  |  |  | U16 | 3,16 | 1 | 2
16888 | Interruption Level, 5% | < 5% |  | U16 | 3,16 | 1 | 1
16889 | Interruption Time, 60s | unused |  | U16 | 3,16 | 1 | 1
16890 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
16891 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
16892 |  |  |  | U16 | 3,16 | 1 | 2
Transient Trigger
16894 | Transient Voltage, HoldOff Time, 20ms | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
16895 | Transient Voltage, Absolute Peak Level, 200% | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
16896 | Transient Voltage, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
16897 | Transient Voltage, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
16898 | Transient Current, HoldOff Time | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
16899 | Transient Current, Absolute Peak Level | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
16900 | Transient Current, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
16901 | Transient Current, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
16902 |  |  |  | U16 | 3,16 | 1 | 12
Recorder
Waveform
16914 | Recorder resolution(32k, 8k) |  |  | U16 | 3,16 | 1 | 1
16915 | Recorded paramater (U or I) |  |  | U16 | 3,16 | 1 | 1
16916 | pre trigger time(0.1s) |  |  | U16 | 3,16 | 1 | 1
16917 | post trigger time(1s) |  |  | U16 | 3,16 | 1 | 1
Disturbance
16918 | Recorder resolution (Half Cycle) |  |  | U16 | 3,16 | 1 | 1
16919 | Recorded parametrs(U or I) |  |  | U16 | 3,16 | 1 | 1
16920 | pre trigger time(100 sample) |  |  | U16 | 3,16 | 1 | 1
16921 | post trigger time(900 sample) |  |  | U16 | 3,16 | 1 | 1
16922 |  |  |  | U16 | 3,16 | 1 | 12
Trend Recorder
16934 | Trend Group #1 Active |  |  | U16 | 3,16 | 1 | 1
16935 | Trend Group #1 Storage Interval |  |  | U16 | 3,16 | 1 | 1
16936 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
16937 | Trend Group #1, Channel #1 |  |  | U16 | 3,16 | 1 | 1
16938 | Trend Group #1, Channel #2 |  |  | U16 | 3,16 | 1 | 1
16939 | Trend Group #1, Channel #3 |  |  | U16 | 3,16 | 1 | 1
16940 | Trend Group #1, Channel #4 |  |  | U16 | 3,16 | 1 | 1
16941 | Trend Group #1, Channel #5 |  |  | U16 | 3,16 | 1 | 1
16942 | Trend Group #1, Channel #6 |  |  | U16 | 3,16 | 1 | 1
16943 | Trend Group #1, Channel #7 |  |  | U16 | 3,16 | 1 | 1
16944 | Trend Group #1, Channel #8 |  |  | U16 | 3,16 | 1 | 1
16945 | Trend Group #1, Channel #9 |  |  | U16 | 3,16 | 1 | 1
16946 | Trend Group #1, Channel #10 |  |  | U16 | 3,16 | 1 | 1
16947 | Trend Group #1, Channel #11 |  |  | U16 | 3,16 | 1 | 1
16948 | Trend Group #1, Channel #12 |  |  | U16 | 3,16 | 1 | 1
16949 | Trend Group #1, Channel #13 |  |  | U16 | 3,16 | 1 | 1
16950 | Trend Group #1, Channel #14 |  |  | U16 | 3,16 | 1 | 1
16951 | Trend Group #1, Channel #15 |  |  | U16 | 3,16 | 1 | 1
16952 | Trend Group #1, Channel #16 |  |  | U16 | 3,16 | 1 | 1
16953 | Trend Group #2 Active |  |  | U16 | 3,16 | 1 | 1
16954 | Trend Group #2 Storage Interval |  |  | U16 | 3,16 | 1 | 1
16955 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
16956 | Trend Group #2, Channel #1 |  |  | U16 | 3,16 | 1 | 1
16957 | Trend Group #2, Channel #2 |  |  | U16 | 3,16 | 1 | 1
16958 | Trend Group #2, Channel #3 |  |  | U16 | 3,16 | 1 | 1
16959 | Trend Group #2, Channel #4 |  |  | U16 | 3,16 | 1 | 1
16960 | Trend Group #2, Channel #5 |  |  | U16 | 3,16 | 1 | 1
16961 | Trend Group #2, Channel #6 |  |  | U16 | 3,16 | 1 | 1
16962 | Trend Group #2, Channel #7 |  |  | U16 | 3,16 | 1 | 1
16963 | Trend Group #2, Channel #8 |  |  | U16 | 3,16 | 1 | 1
16964 | Trend Group #2, Channel #9 |  |  | U16 | 3,16 | 1 | 1
16965 | Trend Group #2, Channel #10 |  |  | U16 | 3,16 | 1 | 1
16966 | Trend Group #2, Channel #11 |  |  | U16 | 3,16 | 1 | 1
16967 | Trend Group #2, Channel #12 |  |  | U16 | 3,16 | 1 | 1
16968 | Trend Group #2, Channel #13 |  |  | U16 | 3,16 | 1 | 1
16969 | Trend Group #2, Channel #14 |  |  | U16 | 3,16 | 1 | 1
16970 | Trend Group #2, Channel #15 |  |  | U16 | 3,16 | 1 | 1
16971 | Trend Group #2, Channel #16 |  |  | U16 | 3,16 | 1 | 1
16972 | Trend Group #3 Active |  |  | U16 | 3,16 | 1 | 1
16973 | Trend Group #3 Storage Interval |  |  | U16 | 3,16 | 1 | 1
16974 |  |  |  | U16 | 3,16 | 1 | 1
16975 | Trend Group #3, Channel #1 |  |  | U16 | 3,16 | 1 | 1
16976 | Trend Group #3, Channel #2 |  |  | U16 | 3,16 | 1 | 1
16977 | Trend Group #3, Channel #3 |  |  | U16 | 3,16 | 1 | 1
16978 | Trend Group #3, Channel #4 |  |  | U16 | 3,16 | 1 | 1
16979 | Trend Group #3, Channel #5 |  |  | U16 | 3,16 | 1 | 1
16980 | Trend Group #3, Channel #6 |  |  | U16 | 3,16 | 1 | 1
16981 | Trend Group #3, Channel #7 |  |  | U16 | 3,16 | 1 | 1
16982 | Trend Group #3, Channel #8 |  |  | U16 | 3,16 | 1 | 1
16983 | Trend Group #3, Channel #9 |  |  | U16 | 3,16 | 1 | 1
16984 | Trend Group #3, Channel #10 |  |  | U16 | 3,16 | 1 | 1
16985 | Trend Group #3, Channel #11 |  |  | U16 | 3,16 | 1 | 1
16986 | Trend Group #3, Channel #12 |  |  | U16 | 3,16 | 1 | 1
16987 | Trend Group #3, Channel #13 |  |  | U16 | 3,16 | 1 | 1
16988 | Trend Group #3, Channel #14 |  |  | U16 | 3,16 | 1 | 1
16989 | Trend Group #3, Channel #15 |  |  | U16 | 3,16 | 1 | 1
16990 | Trend Group #3, Channel #16 |  |  | U16 | 3,16 | 1 | 1
16991 | Trend Group #4 Active |  |  | U16 | 3,16 | 1 | 1
16992 | Trend Group #4 Storage Interval |  |  | U16 | 3,16 | 1 | 1
16993 |  |  |  | U16 | 3,16 | 1 | 1
16994 | Trend Group #4, Channel #1 |  |  | U16 | 3,16 | 1 | 1
16995 | Trend Group #4, Channel #2 |  |  | U16 | 3,16 | 1 | 1
16996 | Trend Group #4, Channel #3 |  |  | U16 | 3,16 | 1 | 1
16997 | Trend Group #4, Channel #4 |  |  | U16 | 3,16 | 1 | 1
16998 | Trend Group #4, Channel #5 |  |  | U16 | 3,16 | 1 | 1
16999 | Trend Group #4, Channel #6 |  |  | U16 | 3,16 | 1 | 1
17000 | Trend Group #4, Channel #7 |  |  | U16 | 3,16 | 1 | 1
17001 | Trend Group #4, Channel #8 |  |  | U16 | 3,16 | 1 | 1
17002 | Trend Group #4, Channel #9 |  |  | U16 | 3,16 | 1 | 1
17003 | Trend Group #4, Channel #10 |  |  | U16 | 3,16 | 1 | 1
17004 | Trend Group #4, Channel #11 |  |  | U16 | 3,16 | 1 | 1
17005 | Trend Group #4, Channel #12 |  |  | U16 | 3,16 | 1 | 1
17006 | Trend Group #4, Channel #13 |  |  | U16 | 3,16 | 1 | 1
17007 | Trend Group #4, Channel #14 |  |  | U16 | 3,16 | 1 | 1
17008 | Trend Group #4, Channel #15 |  |  | U16 | 3,16 | 1 | 1
17009 | Trend Group #4, Channel #16 |  |  | U16 | 3,16 | 1 | 1
17010 |  |  |  | U16 | 3,16 | 1 | 4
Power Quality Report
17014 | Active |  |  | U16 | 3,16 | 1 | 1
17015 | Start Day |  |  | U16 | 3,16 | 1 | 1
17016 |  |  |  | U16 |  | 1 | 8
Alarm Definition
17024 | compare Time Delay(1s) |  |  | U16 | 3,16 | 1 | 1
17025 |  |  |  | U16 |  | 1 | 1
17026 |  |  |  | U16 |  | 1 | 1
17027 |  |  |  | U16 |  | 1 | 1
Alarm Settings
17028 | Alarm Info #1 Channel(0:disabled, >0: enabled) |  |  | U16 | 3,16 | 1 | 1
17029 | Alarm Cond (0: < , 1:>) |  |  | U16 | 3,16 | 1 | 1
17030 | Hysteresis (% of Nominal) |  |  | U16 | 3,16 | 1 | 1
17031 | Alarm Action (None, Relay or Beep) |  |  | U16 | 3,16 | 1 | 1
17032 | Alarm Level |  |  | float | 3,16 | 2 | 1
17034 | Alarm Settings #2 |  |  | U16 | 3,16 | 1 | 6
17040 | Alarm Settings #3 |  |  | U16 | 3,16 | 1 | 6
17046 | Alarm Settings #4 |  |  | U16 | 3,16 | 1 | 6
17052 | Alarm Settings #5 |  |  | U16 | 3,16 | 1 | 6
17058 | Alarm Settings #6 |  |  | U16 | 3,16 | 1 | 6
17064 | Alarm Settings #7 |  |  | U16 | 3,16 | 1 | 6
17070 | Alarm Settings #8 |  |  | U16 | 3,16 | 1 | 6
17076 | Alarm Settings #9 |  |  | U16 | 3,16 | 1 | 6
17082 | Alarm Settings #10 |  |  | U16 | 3,16 | 1 | 6
17088 | Alarm Settings #11 |  |  | U16 | 3,16 | 1 | 6
17094 | Alarm Settings #12 |  |  | U16 | 3,16 | 1 | 6
17100 | Alarm Settings #13 |  |  | U16 | 3,16 | 1 | 6
17106 | Alarm Settings #14 |  |  | U16 | 3,16 | 1 | 6
17112 | Alarm Settings #15 |  |  | U16 | 3,16 | 1 | 6
17118 | Alarm Settings #16 |  |  | U16 | 3,16 | 1 | 6
17124 | Alarm Settings #17 |  |  | U16 | 3,16 | 1 | 6
17130 | Alarm Settings #18 |  |  | U16 | 3,16 | 1 | 6
17136 | Alarm Settings #19 |  |  | U16 | 3,16 | 1 | 6
17142 | Alarm Settings #20 |  |  | U16 | 3,16 | 1 | 6
17148 | Alarm Settings #21 |  |  | U16 | 3,16 | 1 | 6
17154 | Alarm Settings #22 |  |  | U16 | 3,16 | 1 | 6
17160 | Alarm Settings #23 |  |  | U16 | 3,16 | 1 | 6
17166 | Alarm Settings #24 |  |  | U16 | 3,16 | 1 | 6
17172 | Alarm Settings #25 |  |  | U16 | 3,16 | 1 | 6
17178 | Alarm Settings #26 |  |  | U16 | 3,16 | 1 | 6
17184 | Alarm Settings #27 |  |  | U16 | 3,16 | 1 | 6
17190 | Alarm Settings #28 |  |  | U16 | 3,16 | 1 | 6
17196 | Alarm Settings #29 |  |  | U16 | 3,16 | 1 | 6
17202 | Alarm Settings #30 |  |  | U16 | 3,16 | 1 | 6
17208 | Alarm Settings #31 |  |  | U16 | 3,16 | 1 | 6
17214 | Alarm Settings #32 |  |  | U16 | 3,16 | 1 | 6

## #3CH modbus
address | name | 설명 | Unit | TYPE | FC | Word Count | Item Count
Metering
20000 | Time Stamp |  |  | UTC | 3 | 2 | 1
20002 | TYPE |  |  | U16 | 3 | 1 | 1
20003 | STATUS | 1 : online, 0 : offline |  | U16 | 3 | 1 | 1
20004 | Frequency | 라인주파수 | Hz | float | 3 | 2 | 1
20006 | Internal Temp |  | ℃ | float | 3 | 2 | 1
20008 | U1 | 상전압 1 | V | float | 3 | 2 | 1
20010 | U2 | 상전압 2 |  | float | 3 | 2 | 1
20012 | U3 | 상전압 3 |  | float | 3 | 2 | 1
20014 | U~ | 상전압 평균 |  | float | 3 | 2 | 1
20016 | U12 | 선간 전압 12 |  | float | 3 | 2 | 1
20018 | U23 | 선간 전압 23 |  | float | 3 | 2 | 1
20020 | U31 | 선간 전압 31 |  | float | 3 | 2 | 1
20022 | Upp~ | 선간 전압 평균 |  | float | 3 | 2 | 1
20024 | Uunbalance2 |  | % | float | 3 | 2 | 1
20026 | Uunbalance0 |  |  | float | 3 | 2 | 1
20028 | U Zero Sequence Mag. |  |  | float | 3 | 2 | 1
20030 | U Zero Sequence angle |  |  | float | 3 | 2 | 1
20032 | U Positive Sequence Mag. |  |  | float | 3 | 2 | 1
20034 | U Positive Sequence angle |  |  | float | 3 | 2 | 1
20036 | U Negative Sequence Mag |  |  | float | 3 | 2 | 1
20038 | U Negative Sequence angle |  |  | float | 3 | 2 | 1
20040 | Angle U1 |  |  | float | 3 | 2 | 1
20042 | Angle U2 |  |  | float | 3 | 2 | 1
20044 | Angle U3 |  |  | float | 3 | 2 | 1
20046 | U Underdeviation L1 |  | % | float | 3 | 2 | 1
20048 | U Underdeviation L2 |  | % | float | 3 | 2 | 1
20050 | U Underdeviation L3 |  | % | float | 3 | 2 | 1
20052 | U Overdeviation L1 |  | % | float | 3 | 2 | 1
20054 | U Overdeviation L2 |  | % | float | 3 | 2 | 1
20056 | U Overdeviation L3 |  | % | float | 3 | 2 | 1
20058 | I1 | 상전류 1 | A | float | 3 | 2 | 1
20060 | I2 | 상전류 2 |  | float | 3 | 2 | 1
20062 | I3 | 상전류 3 |  | float | 3 | 2 | 1
20064 | I~ |  |  | float | 3 | 2 | 1
20066 | I total (I1+I2+I3) |  |  | float | 3 | 2 | 1
20068 | In(Measured) |  |  | float | 3 | 2 | 1 | 1. 5A: -3P4W(In) -3P3W(Ig), 2. AT/VT: Ig로 사용
20070 | In(Calculated) | Ia+Ib+Ic+In = Ig |  | float | 3 | 2 | 1 | 1. 5A: -3P4W(Ig=Ia+Ib+Ic+In), -3P3W(Ig=Ia+Ib+Ic), 2. AT/VT: 5A와 동일
20072 | Ig |  |  | float | 3 | 2 | 1
20074 | I Zero Sequence Mag |  |  | float | 3 | 2 | 1
20076 | I Zero Sequence angle |  |  | float | 3 | 2 | 1
20078 | I Positive Sequence Mag. |  |  | float | 3 | 2 | 1
20080 | I Positive Sequence angle |  |  | float | 3 | 2 | 1
20082 | I Negative Sequence Mag. |  |  | float | 3 | 2 | 1
20084 | I Negative Sequence angle |  |  | float | 3 | 2 | 1
20086 | Angle I1 |  |  | float | 3 | 2 | 1
20088 | Angle I2 |  |  | float | 3 | 2 | 1
20090 | Angle I3 |  |  | float | 3 | 2 | 1
20092 | Iunbalance2 |  | % | float | 3 | 2 | 1
20094 | Iunbalance0 |  |  | float | 3 | 2 | 1
20096 | P1 | 유효전력 P1 | W | float | 3 | 2 | 1
20098 | P2 | 유효전력 P2 |  | float | 3 | 2 | 1
20100 | P3 | 유효전력 P3 |  | float | 3 | 2 | 1
20102 | P total | 유효전력 P-total |  | float | 3 | 2 | 1
20104 | fP1 |  |  | float | 3 | 2 | 1
20106 | fP2 |  |  | float | 3 | 2 | 1
20108 | fP3 |  |  | float | 3 | 2 | 1
20110 | fP total |  |  | float | 3 | 2 | 1
20112 | Q1 | 무효전력 Q1 | VAR | float | 3 | 2 | 1
20114 | Q2 | 무효전력 Q2 |  | float | 3 | 2 | 1
20116 | Q3 | 무효전력 Q3 |  | float | 3 | 2 | 1
20118 | Q total | 무효전력 Q-total |  | float | 3 | 2 | 1
20120 | fQ1 |  |  | float | 3 | 2 | 1
20122 | fQ2 |  |  | float | 3 | 2 | 1
20124 | fQ3 |  |  | float | 3 | 2 | 1
20126 | fQ total |  |  | float | 3 | 2 | 1
20128 | S1 | 피상전력 S1 | VA | float | 3 | 2 | 1
20130 | S2 | 피상전력 S2 |  | float | 3 | 2 | 1
20132 | S3 | 피상전력 S3 |  | float | 3 | 2 | 1
20134 | S total | 피상전력 S-total |  | float | 3 | 2 | 1
20136 | fS1 |  |  | float | 3 | 2 | 1
20138 | fS2 |  |  | float | 3 | 2 | 1
20140 | fS3 |  |  | float | 3 | 2 | 1
20142 | fS total |  |  | float | 3 | 2 | 1
20144 | PF1 | 역률 PF1 | % | float | 3 | 2 | 1
20146 | PF2 | 역률 PF2 |  | float | 3 | 2 | 1
20148 | PF3 | 역률 PF3 |  | float | 3 | 2 | 1
20150 | PF total | 역률 PF-total |  | float | 3 | 2 | 1
20152 | dPF1 |  | % | float | 3 | 2 | 1
20154 | dPF2 |  |  | float | 3 | 2 | 1
20156 | dPF3 |  |  | float | 3 | 2 | 1
20158 | dPF total |  |  | float | 3 | 2 | 1
20160 | deformed Power D L1 |  | W | float | 3 | 2 | 1 | S=sqrt {P^{2}+Q^{2}+D^{2}}
20162 | deformed Power D L2 |  |  | float | 3 | 2 | 1
20164 | deformed Power D L3 |  |  | float | 3 | 2 | 1
20166 | deformed Power D Total |  |  | float | 3 | 2 | 1
20168 | Power Angle(atan(fPt,fQt) L1 |  | Degree | float | 3 | 2 | 1 | Angle between fundamental phase voltage and phase current
20170 | Power Angle(atan(fPt,fQt) L2 |  |  | float | 3 | 2 | 1
20172 | Power Angle(atan(fPt,fQt) L3 |  |  | float | 3 | 2 | 1
20174 |  |  |  | float | 3 | 2 | 1
20176 | THD V1 |  | % | float | 3 | 2 | 1
20178 | THD V2 |  |  | float | 3 | 2 | 1 | Chip에서 제공하는 결과 사용
20180 | THD V3 |  |  | float | 3 | 2 | 1
20182 | THD V12 |  |  | float | 3 | 2 | 1
20184 | THD V23 |  |  | float | 3 | 2 | 1
20186 | THD V31 |  |  | float | 3 | 2 | 1
20188 | CF V1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
20190 | CF V2 |  |  | float | 3 | 2 | 1
20192 | CF V3 |  |  | float | 3 | 2 | 1
20194 | CF V12 |  |  | float | 3 | 2 | 1
20196 | CF V23 |  |  | float | 3 | 2 | 1
20198 | CF V31 |  |  | float | 3 | 2 | 1
20200 | THD I1 |  |  | float | 3 | 2 | 1
20202 | THD I2 |  |  | float | 3 | 2 | 1
20204 | THD I3 |  |  | float | 3 | 2 | 1
20206 | TDD I1 |  |  | float | 3 | 2 | 1
20208 | TDD I2 |  |  | float | 3 | 2 | 1
20210 | TDD I3 |  |  | float | 3 | 2 | 1
20212 | K I1 | K-FACTOR : 고조파 허용율 |  | float | 3 | 2 | 1
20214 | K I2 |  |  | float | 3 | 2 | 1
20216 | K I3 |  |  | float | 3 | 2 | 1
20218 | CF I1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
20220 | CF I2 |  |  | float | 3 | 2 | 1
20222 | CF I3 |  |  | float | 3 | 2 | 1
20224 | fU1 | 기본파 U1 | V | float | 3 | 2 | 1
20226 | fU2 | 기본파 U2 |  | float | 3 | 2 | 1
20228 | fU3 | 기본파 U3 |  | float | 3 | 2 | 1
20230 | fU~ | 기본파 전압 평균 |  | float | 3 | 2 | 1
20232 | fI1 | 기본파 I1 | A | float | 3 | 2 | 1
20234 | fI2 | 기본파 I2 |  | float | 3 | 2 | 1
20236 | fI3 | 기본파 I3 |  | float | 3 | 2 | 1
20238 | fI~ | 기본파 전류 평균 |  | float | 3 | 2 | 1
Energy
20240 | import kwh(0 ~ 999,999,999.9 kw) | 누적 유효전력량 |  | U32 | 3 | 2 | 1
20242 | export kwh |  |  | U32 | 3 | 2 | 1
20244 | import kvarh |  |  | U32 | 3 | 2 | 1
20246 | export kvarh |  |  | U32 | 3 | 2 | 1
20248 | kvah |  |  | U32 | 3 | 2 | 1
20250 |  |  |  | U32 | 3 | 2 | 1
20252 | import kwh this month |  |  | U32 | 3 | 2 | 1
20254 | export kwh this month |  |  | U32 | 3 | 2 | 1
20256 | import kvarh this month |  |  | U32 | 3 | 2 | 1
20258 | export kvarh this month |  |  | U32 | 3 | 2 | 1
20260 | kvah this month |  |  | U32 | 3 | 2 | 1
20262 |  |  |  | U32 | 3 | 2 | 1
20264 | import kwh last month |  |  | U32 | 3 | 2 | 1 | Demand P(import)
20266 | export kwh last month |  |  | U32 | 3 | 2 | 1
20268 | import kvarh last month |  |  | U32 | 3 | 2 | 1
20270 | export kvarh last month |  |  | U32 | 3 | 2 | 1
20272 | kvah last month |  |  | U32 | 3 | 2 | 1
20274 |  |  |  | U32 | 3 | 2 | 1
20276 | import kwh | 0~999,999,999.999 kw |  | U64 | 3 | 4 | 1 | Demand P(import)
20280 | export kwh |  |  | U64 | 3 | 4 | 1
20284 | import kvarh |  |  | U64 | 3 | 4 | 1
20288 | export kvarh |  |  | U64 | 3 | 4 | 1
20292 | kvah |  |  | U64 | 3 | 4 | 1
20296 |  |  |  | U64 | 3 | 4 | 1
Demand
20300 | Time Stamp |  |  | UTC | 3 | 2 | 1
20302 | Max Demand P(import) |  |  | float | 3 | 2 | 1
20304 | Time Stamp |  |  | UTC | 3 | 2 | 1
20306 | Max Demand P(export) |  |  | float | 3 | 2 | 1
20308 | Time Stamp |  |  | UTC | 3 | 2 | 1
20310 | Max Demand Q(import) |  |  | float | 3 | 2 | 1
20312 | Time Stamp |  |  | UTC | 3 | 2 | 1
20314 | Max Demand Q(export) |  |  | float | 3 | 2 | 1
20316 | Time Stamp |  |  | UTC | 3 | 2 | 1
20318 | Max Demand S |  |  | float | 3 | 2 | 1
20320 | Time Stamp |  |  | UTC | 3 | 2 | 1
20322 | Max Demand I1 |  |  | float | 3 | 2 | 1
20324 | Time Stamp |  |  | UTC | 3 | 2 | 1
20326 | Max Demand I2 |  |  | float | 3 | 2 | 1
20328 | Time Stamp |  |  | UTC | 3 | 2 | 1
20330 | Max Demand I3 |  |  | float | 3 | 2 | 1
20332 | Demand time stamp |  |  | UTC | 3 | 2 | 1
20334 | Demand P(import) |  |  | float | 3 | 2 | 1
20336 | Demand P(export) |  |  | float | 3 | 2 | 1 | 최근 24시간 그래프 그린다
20338 | Demand Q(import) |  |  | float | 3 | 2 | 1
20340 | Demand Q(export) |  |  | float | 3 | 2 | 1
20342 | Demand S(export) |  |  | float | 3 | 2 | 1
20344 | Demand I1 |  |  | float | 3 | 2 | 1
20346 | Demand I2 |  |  | float | 3 | 2 | 1
20348 | Demand I3 |  |  | float | 3 | 2 | 1
20350 | Present Demand P(import) |  |  | float | 3 | 2 | 1
20352 | Present Demand P(export) |  |  | float | 3 | 2 | 1
20354 | Present Demand Q(import) |  |  | float | 3 | 2 | 1
20356 | Present Demand Q(export) |  |  | float | 3 | 2 | 1
20358 | Present Demand S(export) |  |  | float | 3 | 2 | 1
20360 | Forecast Demand P(export) |  |  | float | 3 | 2 | 1
20362 | Demand P 15m(import) |  |  | float | 3 | 2 | 1
20364 |  |  |  | float | 3 | 2 | 1
20366 |  |  |  | float | 3 | 2 | 1
20368 | Time Stamp(Demand Log 시작일) |  |  | U32 | 3 | 2 | 1
20370 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
20562 |  |  |  | float | 3 | 2 | 19
Voltage Quality RealTime Value
20600 | Voltage Under Deviation L1 |  | % | float | 3 | 2 | 1
20602 | Voltage Under Deviation L2 |  | % | float | 3 | 2 | 1
20604 | Voltage Under Deviation L3 |  | % | float | 3 | 2 | 1
20606 | Voltage Under Value L1 |  | rms | float | 3 | 2 | 1
20608 | Voltage Under Value L2 |  | rms | float | 3 | 2 | 1
20610 | Voltage Under Value L3 |  | rms | float | 3 | 2 | 1
20612 | Voltage Over Deviation L1 |  | % | float | 3 | 2 | 1
20614 | Voltage Over Deviation L2 |  | % | float | 3 | 2 | 1
20616 | Voltage Over Deviation L3 |  | % | float | 3 | 2 | 1
20618 | Voltage Over Value L1 |  | rms | float | 3 | 2 | 1
20620 | Voltage Over Value L2 |  | rms | float | 3 | 2 | 1
20622 | Voltage Over Value L3 |  | rms | float | 3 | 2 | 1
20624 | Flickers Pi L1 | 150/180 Cycles |  | float | 3 | 2 | 1
20626 | Flickers Pi L2 |  |  | float | 3 | 2 | 1
20628 | Flickers Pi L3 |  |  | float | 3 | 2 | 1
20630 | Flicker Pst L1 | 10min |  | float | 3 | 2 | 1
20632 | Flicker Pst L2 |  |  | float | 3 | 2 | 1
20634 | Flicker Pst L3 |  |  | float | 3 | 2 | 1
20636 | Flicker Plt L1 | 2hr |  | float | 3 | 2 | 1 | 최근 24시간 그래프 그린다
20638 | Flicker Plt L2 |  |  | float | 3 | 2 | 1
20640 | Flicker Plt L3 |  |  | float | 3 | 2 | 1
20642 | Signaling Volt L1 | Magnitude of current 10/12 cycles as a percentage of nominal voltage. |  | float | 3 | 2 | 1
20644 | Signaling Volt L2 |  |  | float | 3 | 2 | 1
20646 | Signaling Volt L3 |  |  | float | 3 | 2 | 1
20648 | Signaling Volt Max L1 | Maximum magnitude of MSV from recording started as a percentage of nominal voltage |  | float | 3 | 2 | 1
20650 | Signaling Volt Max L2 |  |  | float | 3 | 2 | 1
20652 | Signaling Volt Max L3 |  |  | float | 3 | 2 | 1
20654 |  |  |  | float | 3 | 2 | 23
EN50160 This Week
20700 | start date |  |  | UTC | 3 | 2 | 1
20702 | end date |  |  | UTC | 3 | 2 | 1
20704 | status&compliance | bit 0: Freq Var1 bit 1: Freq Var2 bit 2: Volt Var1 L1 bit 3: Volt Var1 L2 bit 4: Volt Var1 L3 bit 5: Volt Var2 L1 bit 6: Volt Var2 L2 bit 7: Volt Var2 L3 bit 8: Unbalance bit 9: Volt THD L1 bit 10: Volt THD L2 bit 11: Volt THD L3 bit 12: Volt HD L1 bit 13: Volt HD L2 bit 14: Volt HD L3 bit 15: Pst L1 bit 16: Pst L2 bit 17: Pst L3 bit 18: Plt L1 bit 19: Plt L2 bit 20: Plt L3 bit 21: SigVolt L1 bit 22: SigVolt L2 bit 23: SigVolt L3 bit 31: Complete [status] 0: OK 1: failed |  | U32 | 3 | 2 | 1
20706 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1 | 95%/Week
20707 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1 | Info Only
20708 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
20709 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
20710 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
20711 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
20712 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
20713 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1 | Info Only
20714 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
20715 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
20716 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
20717 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
20718 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
20719 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
20720 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
20721 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
20722 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
20723 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
20724 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
20725 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
20726 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
20727 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
20728 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
20729 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
20730 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
20731 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1 | 99%/Day
20732 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
20733 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
20734 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
20735 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
20736 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
20737 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
20738 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
20739 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
20740 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
20741 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
20742 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
20743 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
20744 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
20745 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
20746 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
20747 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
20748 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
20749 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
EN50160 Last Week
20750 | start date |  |  | UTC | 3 | 2 | 1
20752 | end date |  |  | UTC | 3 | 2 | 1
20754 | status |  |  | U16 | 3 | 1 | 1
20755 | compilance |  |  | U16 | 3 | 1 | 1
20756 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1
20757 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1
20758 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
20759 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
20760 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1
20761 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
20762 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
20763 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1
20764 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
20765 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
20766 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1
20767 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
20768 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
20769 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1
20770 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
20771 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
20772 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1
20773 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
20774 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
20775 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1
20776 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
20777 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
20778 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1
20779 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
20780 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
20781 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1
20782 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
20783 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
20784 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
20785 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
20786 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
20787 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
20788 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
20789 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
20790 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
20791 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
20792 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
20793 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
20794 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
20795 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
20796 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
20797 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
20798 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
20799 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
Harmonics
20800 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
20864 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
20928 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
20992 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
21056 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
21120 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
21184 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
21248 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
21312 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
21376 |  |  |  | S16 | 3 | 1 | 24
Inter Harmonics
21400 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
21464 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
21528 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
21592 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
21656 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
21720 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
21784 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
21848 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
21912 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
21976 |  |  |  | S16 | 3 | 1 | 24
Max/Min
22000 | fr |  |  | U16 | 3 | 1 | 1
22001 | re |  |  | U16 | 3 | 1 | 1
22002 | Reset TimeStamp |  |  | UTC | 3 | 2 | 1
22004 | Frequency |  |  | float | 3 | 2 | 4
22012 | Temp |  |  | float | 3 | 2 | 4
22020 | U1 |  |  | float | 3 | 2 | 4
22028 | U2 |  |  | float | 3 | 2 | 4
22036 | U3 |  |  | float | 3 | 2 | 4 | http://www.relaytech.com/symcomp_calculator.htm
22044 | U~ |  |  | float | 3 | 2 | 4
22052 | U12 |  |  | float | 3 | 2 | 4
22060 | U23 |  |  | float | 3 | 2 | 4
22068 | U31 |  |  | float | 3 | 2 | 4
22076 | Upp~ |  |  | float | 3 | 2 | 4
22084 | I1 |  |  | float | 3 | 2 | 4
22092 | I2 |  |  | float | 3 | 2 | 4
22100 | I3 |  |  | float | 3 | 2 | 4
22108 | I~ |  |  | float | 3 | 2 | 4
22116 | I total |  |  | float | 3 | 2 | 4
22124 | In |  |  | float | 3 | 2 | 4
22132 | Isum |  |  | float | 3 | 2 | 4
22140 | P1 |  |  | float | 3 | 2 | 4
22148 | P2 |  |  | float | 3 | 2 | 4
22156 | P3 |  |  | float | 3 | 2 | 4
22164 | P total |  |  | float | 3 | 2 | 4
22172 | Q1 |  |  | float | 3 | 2 | 4
22180 | Q2 |  |  | float | 3 | 2 | 4
22188 | Q3 |  |  | float | 3 | 2 | 4
22196 | Q total |  |  | float | 3 | 2 | 4
22204 | S1 |  |  | float | 3 | 2 | 4
22212 | S2 |  |  | float | 3 | 2 | 4
22220 | S3 |  |  | float | 3 | 2 | 4
22228 | S total |  |  | float | 3 | 2 | 4
22236 | PF L1 |  |  | float | 3 | 2 | 4
22244 | PF L2 |  |  | float | 3 | 2 | 4
22252 | PF L3 |  |  | float | 3 | 2 | 4
22260 | PF total |  |  | float | 3 | 2 | 4
22268 | THD U1 |  |  | float | 3 | 2 | 4
22276 | THD U2 |  |  | float | 3 | 2 | 4
22284 | THD U3 |  |  | float | 3 | 2 | 4
22292 | THD U12 |  |  | float | 3 | 2 | 4
22300 | THD U23 |  |  | float | 3 | 2 | 4
22308 | THD U31 |  |  | float | 3 | 2 | 4
22316 | THD I1 |  |  | float | 3 | 2 | 4
22324 | THD I2 |  |  | float | 3 | 2 | 4
22332 | THD I3 |  |  | float | 3 | 2 | 4
22340 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
22342 | reserved |  |  | U16 | 3 | 1 | 1
22343 | CRC |  |  | U16 | 3 | 1 | 1
22344 |  |  |  | U16 | 3 | 1 | 6
alarm status
22350 | fr |  |  | U16 | 3 | 1 | 1
22351 | re |  |  | U16 | 3 | 1 | 1
22352 | reset Ts |  |  | UTC | 3 | 2 | 1
22354 | Alarm State #1 | Alarm Channel |  | U16 | 3 | 1 | 1
22355 |  | Alarm Condition |  | U16 | 3 | 1 | 1
22356 |  | Alarm Level |  | float | 3 | 2 | 1
22358 |  | Alarm Status |  | U16 | 3 | 1 | 1
22359 |  | Alarm Count |  | U16 | 3 | 1 | 1
22360 | Alarm State #2 |  |  | U16 | 3 | 1 | 6
22366 | Alarm State #3 |  |  | U16 | 3 | 1 | 6
22372 | Alarm State #4 |  |  | U16 | 3 | 1 | 6
22378 | Alarm State #5 |  |  | U16 | 3 | 1 | 6
22384 | Alarm State #6 |  |  | U16 | 3 | 1 | 6
22390 | Alarm State #7 |  |  | U16 | 3 | 1 | 6
22396 | Alarm State #8 |  |  | U16 | 3 | 1 | 6
22402 | Alarm State #9 |  |  | U16 | 3 | 1 | 6
22408 | Alarm State #10 |  |  | U16 | 3 | 1 | 6
22414 | Alarm State #11 |  |  | U16 | 3 | 1 | 6
22420 | Alarm State #12 |  |  | U16 | 3 | 1 | 6
22426 | Alarm State #13 |  |  | U16 | 3 | 1 | 6
22432 | Alarm State #14 |  |  | U16 | 3 | 1 | 6
22438 | Alarm State #15 |  |  | U16 | 3 | 1 | 6
22444 | Alarm State #16 |  |  | U16 | 3 | 1 | 6
22450 | Alarm State #17 |  |  | U16 | 3 | 1 | 6
22456 | Alarm State #18 |  |  | U16 | 3 | 1 | 6
22462 | Alarm State #19 |  |  | U16 | 3 | 1 | 6
22468 | Alarm State #20 |  |  | U16 | 3 | 1 | 6
22474 | Alarm State #21 |  |  | U16 | 3 | 1 | 6
22480 | Alarm State #22 |  |  | U16 | 3 | 1 | 6
22486 | Alarm State #23 |  |  | U16 | 3 | 1 | 6
22492 | Alarm State #24 |  |  | U16 | 3 | 1 | 6
22498 | Alarm State #25 |  |  | U16 | 3 | 1 | 6
22504 | Alarm State #26 |  |  | U16 | 3 | 1 | 6
22510 | Alarm State #27 |  |  | U16 | 3 | 1 | 6
22516 | Alarm State #28 |  |  | U16 | 3 | 1 | 6
22522 | Alarm State #29 |  |  | U16 | 3 | 1 | 6
22528 | Alarm State #30 |  |  | U16 | 3 | 1 | 6
22534 | Alarm State #31 |  |  | U16 | 3 | 1 | 6
22540 | Alarm State #32 |  |  | U16 | 3 | 1 | 6
22546 | update Ts |  |  | U32 | 3 | 2 | 1
22548 | Global Alarm Status | (alarm 하나라도 있으면 1, 아니면 0) |  | U16 | 3 | 1 | 1
22549 |  |  |  | U16 | 3 | 1 | 1
alarm log
22550 | fr | 0 ~ 1023 |  | U16 | 3 | 1 | 1
22551 | re | 0 ~ 1023 |  | U16 | 3 | 1 | 1
22552 | count | 전체 log 수 |  | U16 | 3 | 1 | 1
22553 | seq |  |  | U16 | 3 | 1 | 1
22554 | Alarm Log #1 | Time Stamp |  | UTC | 3 | 2 | 1 | 2019-5-11변경
22556 |  | status |  | U16 | 3 | 1 | 1
22557 |  | Alarm Channel & Condition |  | U16 | 3 | 1 | 1
22558 |  | level |  | float | 3 | 2 | 1
22560 |  | Value |  | float | 3 | 2 | 1
22562 | Alarm Log #2 |  |  | U16 | 3 | 1 | 8
22570 | Alarm Log #3 |  |  | U16 | 3 | 1 | 8
22578 | Alarm Log #4 |  |  | U16 | 3 | 1 | 8
22586 | Alarm Log #5 |  |  | U16 | 3 | 1 | 8
22594 | Alarm Log #6 |  |  | U16 | 3 | 1 | 8
22602 | Alarm Log #7 |  |  | U16 | 3 | 1 | 8
22610 | Alarm Log #8 |  |  | U16 | 3 | 1 | 8
22618 | Alarm Log #9 |  |  | U16 | 3 | 1 | 8
22626 | Alarm Log #10 |  |  | U16 | 3 | 1 | 8
22634 | Alarm Log #11 |  |  | U16 | 3 | 1 | 8
22642 | Alarm Log #12 |  |  | U16 | 3 | 1 | 8
22650 | Alarm Log #13 |  |  | U16 | 3 | 1 | 8
22658 | Alarm Log #14 |  |  | U16 | 3 | 1 | 8
22666 | Alarm Log #15 |  |  | U16 | 3 | 1 | 8
22674 | Alarm Log #16 |  |  | U16 | 3 | 1 | 8
22682 | Alarm Log #17 |  |  | U16 | 3 | 1 | 8
22690 | Alarm Log #18 |  |  | U16 | 3 | 1 | 8
22698 | Alarm Log #19 |  |  | U16 | 3 | 1 | 8
22706 | Alarm Log #20 |  |  | U16 | 3 | 1 | 8
22714 | Alarm Log #21 |  |  | U16 | 3 | 1 | 8
22722 | Alarm Log #22 |  |  | U16 | 3 | 1 | 8
22730 | Alarm Log #23 |  |  | U16 | 3 | 1 | 8
22738 | Alarm Log #24 |  |  | U16 | 3 | 1 | 8
22746 | Alarm Log #25 |  |  | U16 | 3 | 1 | 8
22754 | Alarm Log #26 |  |  | U16 | 3 | 1 | 8
22762 | Alarm Log #27 |  |  | U16 | 3 | 1 | 8
22770 | Alarm Log #28 |  |  | U16 | 3 | 1 | 8
22778 | Alarm Log #29 |  |  | U16 | 3 | 1 | 8
22786 | Alarm Log #30 |  |  | U16 | 3 | 1 | 8
22794 | Alarm Log #31 |  |  | U16 | 3 | 1 | 8
22802 | Alarm Log #32 |  |  | U16 | 3 | 1 | 8
22810 |  |  |  | U16 | 3 | 1 | 40
이벤트 리스트
22850 | fr | 0 ~ 1023 |  | U16 | 3 | 1 | 1
22851 | re | 0 ~ 1023 |  | U16 | 3 | 1 | 1
22852 | count | 0 ~ 1023 |  | U16 | 3 | 1 | 1
22853 | seq |  |  | U16 | 3 | 1 | 1
PQ 이벤트(Sag, Swell, Transient, OC)
22854 | start ts |  |  | UTC | 3 | 2 | 1
22856 | start ts(ms) |  |  | U16 | 3 | 1 | 1
22857 | duration |  |  | U16 | 3 | 1 | 1
22858 | type | 1 : E_SAG 2 : E_SWELL 3 : E_sINTR 4 : E_lINTR 5 : E_OC 6 : E_RVC 7 : E_TrV 8 : E_TrC |  | U16 | 3 | 1 | 1
22859 | mask |  |  | U16 | 3 | 1 | 1
22860 | Level 1 |  |  | float | 3 | 2 | 1
22862 | Level 2 |  |  | float | 3 | 2 | 1
22864 | Level 3 |  |  | float | 3 | 2 | 1
22866 | PQ Event #2 |  |  | U16 | 3 | 1 | 12
22878 | PQ Event #3 |  |  | U16 | 3 | 1 | 12
22890 | PQ Event #4 |  |  | U16 | 3 | 1 | 12
22902 | PQ Event #5 |  |  | U16 | 3 | 1 | 12
22914 | PQ Event #6 |  |  | U16 | 3 | 1 | 12
22926 | PQ Event #7 |  |  | U16 | 3 | 1 | 12
22938 | PQ Event #8 |  |  | U16 | 3 | 1 | 12
22950 | PQ Event #9 |  |  | U16 | 3 | 1 | 12
22962 | PQ Event #10 |  |  | U16 | 3 | 1 | 12
22974 | PQ Event #11 |  |  | U16 | 3 | 1 | 12
22986 | PQ Event #12 |  |  | U16 | 3 | 1 | 12
22998 | PQ Event #13 |  |  | U16 | 3 | 1 | 12
23010 | PQ Event #14 |  |  | U16 | 3 | 1 | 12
23022 | PQ Event #15 |  |  | U16 | 3 | 1 | 12
23034 | PQ Event #16 |  |  | U16 | 3 | 1 | 12
23046 | PQ Event #17 |  |  | U16 | 3 | 1 | 12
23058 | PQ Event #18 |  |  | U16 | 3 | 1 | 12
23070 | PQ Event #19 |  |  | U16 | 3 | 1 | 12
23082 | PQ Event #20 |  |  | U16 | 3 | 1 | 12
23094 | PQ Event #21 |  |  | U16 | 3 | 1 | 12
23106 | PQ Event #22 |  |  | U16 | 3 | 1 | 12
23118 | PQ Event #23 |  |  | U16 | 3 | 1 | 12
23130 | PQ Event #24 |  |  | U16 | 3 | 1 | 12
23142 | PQ Event #25 |  |  | U16 | 3 | 1 | 12
23154 | PQ Event #26 |  |  | U16 | 3 | 1 | 12
23166 | PQ Event #27 |  |  | U16 | 3 | 1 | 12
23178 | PQ Event #28 |  |  | U16 | 3 | 1 | 12
23190 | PQ Event #29 |  |  | U16 | 3 | 1 | 12
23202 | PQ Event #30 |  |  | U16 | 3 | 1 | 12
23214 | PQ Event #31 |  |  | U16 | 3 | 1 | 12
23226 | PQ Event #32 |  |  | U16 | 3 | 1 | 12
23238 |  |  |  | U16 | 3 | 1 | 2
PQ Event Counter
23240 |  |  |  | U16 | 3 | 1 | 1
23241 |  |  |  | U16 | 3 | 1 | 1
23242 |  |  |  | U16 | 3 | 1 | 1
23243 | Sag Coount |  |  | U16 | 3 | 1 | 1
23244 | Swell Count |  |  | U16 | 3 | 1 | 1
23245 |  |  |  | U16 | 3 | 1 | 1
23246 |  |  |  | U16 | 3 | 1 | 1
23247 |  |  |  | U16 | 3 | 1 | 1
23248 |  |  |  | U16 | 3 | 1 | 1
23249 |  |  |  | U16 | 3 | 1 | 1
Wave Sample | [7 empty] | 32K: 67,107,786 8K: 74,518,668 첫번째 번지 접근시 wave data를 modbus map으로 load 한다
23250 | Wave Form V1 (160 sample) |  |  | S16 | 3 | 1 | 160
23410 | Wave Form V2 (160 sample) |  |  | S16 | 3 | 1 | 160
23570 | Wave Form V3 (160 sample) |  |  | S16 | 3 | 1 | 160
23730 | Wave Form V12 (160 sample) |  |  | S16 | 3 | 1 | 160
23890 | Wave Form V23 (160 sample) |  |  | S16 | 3 | 1 | 160
24050 | Wave Form V31 (160 sample) |  |  | S16 | 3 | 1 | 160
24210 | Wave Form I1 (160 sample) |  |  | S16 | 3 | 1 | 160
24370 | Wave Form I2 (160 sample) |  |  | S16 | 3 | 1 | 160
24530 | Wave Form I3 (160 sample) |  |  | S16 | 3 | 1 | 160
24690 | vscale |  |  | float | 3 | 2 | 1
24692 | iscale |  |  | float | 3 | 2 | 1
24694 |  |  |  | S16 | 3 | 1 | 6
월간리포트 생성위한 10분 평균
24700 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
24702 | U1 |  |  | float | 3 | 2 | 1
24704 | U2 |  |  | float | 3 | 2 | 1
24706 | U3 |  |  | float | 3 | 2 | 1
24708 | U THD1 |  |  | float | 3 | 2 | 1
24710 | U THD2 |  |  | float | 3 | 2 | 1
24712 | U THD3 |  |  | float | 3 | 2 | 1
24714 | Upp THD1 |  |  | float | 3 | 2 | 1
24716 | Upp THD2 |  |  | float | 3 | 2 | 1
24718 | Upp THD3 |  |  | float | 3 | 2 | 1
24720 | U Unbal Uu |  |  | float | 3 | 2 | 1
24722 | U Unbal Uo |  |  | float | 3 | 2 | 1
24724 | I1 |  |  | float | 3 | 2 | 1
24726 | I2 |  |  | float | 3 | 2 | 1
24728 | I3 |  |  | float | 3 | 2 | 1
24730 | In |  |  | float | 3 | 2 | 1
24732 | I THD1 |  |  | float | 3 | 2 | 1
24734 | I THD2 |  |  | float | 3 | 2 | 1
24736 | I THD3 |  |  | float | 3 | 2 | 1
24738 | I TDD1 |  |  | float | 3 | 2 | 1
24740 | I TDD2 |  |  | float | 3 | 2 | 1
24742 | I TDD3 |  |  | float | 3 | 2 | 1
24744 | K-factor 1 |  |  | float | 3 | 2 | 1
24746 | K-factor 2 |  |  | float | 3 | 2 | 1
24748 | K-factor 3 |  |  | float | 3 | 2 | 1
24750 | I Unbal Iu |  |  | float | 3 | 2 | 1
24752 | I Unbal Io |  |  | float | 3 | 2 | 1
24754 | kw imp |  |  | float | 3 | 2 | 1
24756 | kw exp |  |  | float | 3 | 2 | 1
24758 | kvar lag |  |  | float | 3 | 2 | 1
24760 | kvar lead |  |  | float | 3 | 2 | 1
24762 | kVA |  |  | float | 3 | 2 | 1
24764 | PF |  |  | float | 3 | 2 | 1
24766 | dPF |  |  | float | 3 | 2 | 1
24768 | temperature #1 |  |  | float | 3 | 2 | 1
24770 | temperature #2 |  |  | float | 3 | 2 | 1
24772 | temperature #3 |  |  | float | 3 | 2 | 1
24774 | temperature #4 |  |  | float | 3 | 2 | 1
24776 | temperature #5 |  |  | float | 3 | 2 | 1 | *통신이 끊어진 경우 복구를 위해 사용된다
24778 | Harmonics V1 |  |  | S16 | 3 | 1 | 24
24802 | Harmonics V2 |  |  | S16 | 3 | 1 | 24 | demand
24826 | Harmonics V3 |  |  | S16 | 3 | 1 | 24
24850 | Harmonics V12 |  |  | S16 | 3 | 1 | 24
24874 | Harmonics V23 |  |  | S16 | 3 | 1 | 24
24898 | Harmonics V31 |  |  | S16 | 3 | 1 | 24
24922 | Harmonics I1 |  |  | S16 | 3 | 1 | 24
24946 | Harmonics I2 |  |  | S16 | 3 | 1 | 24
24970 | Harmonics I3 |  |  | S16 | 3 | 1 | 24
24994 |  |  |  | U16 | 3 | 1 | 6
Energy log
25000 | Time Stamp |  |  | UTC | 3 | 2 | 1
25002 | kwh import |  |  | float | 3 | 2 | 1
25004 | kvarh lag |  |  | float | 3 | 2 | 1
25006 | kvarh lead |  |  | float | 3 | 2 | 1
25008 | kVAh |  |  | float | 3 | 2 | 1
25010 | energy log last day 01h |  |  | float | 3 | 2 | 4
25018 | energy log last day 02h |  |  | float | 3 | 2 | 4
25026 | energy log last day 03h |  |  | float | 3 | 2 | 4
25034 | energy log last day 04h |  |  | float | 3 | 2 | 4
25042 | energy log last day 05h |  |  | float | 3 | 2 | 4
25050 | energy log last day 06h |  |  | float | 3 | 2 | 4
25058 | energy log last day 07h |  |  | float | 3 | 2 | 4
25066 | energy log last day 08h |  |  | float | 3 | 2 | 4
25074 | energy log last day 09h |  |  | float | 3 | 2 | 4
25082 | energy log last day 10h |  |  | float | 3 | 2 | 4
25090 | energy log last day 11h |  |  | float | 3 | 2 | 4
25098 | energy log last day 12h |  |  | float | 3 | 2 | 4
25106 | energy log last day 13h |  |  | float | 3 | 2 | 4
25114 | energy log last day 14h |  |  | float | 3 | 2 | 4
25122 | energy log last day 15h |  |  | float | 3 | 2 | 4
25130 | energy log last day 16h |  |  | float | 3 | 2 | 4
25138 | energy log last day 17h |  |  | float | 3 | 2 | 4
25146 | energy log last day 18h |  |  | float | 3 | 2 | 4
25154 | energy log last day 19h |  |  | float | 3 | 2 | 4
25162 | energy log last day 20h |  |  | float | 3 | 2 | 4
25170 | energy log last day 21h |  |  | float | 3 | 2 | 4
25178 | energy log last day 22h |  |  | float | 3 | 2 | 4
25186 | energy log last day 23h |  |  | float | 3 | 2 | 4
25194 |  |  |  | U16 | 3 | 1 | 6
25200 | Time Stamp |  |  | UTC | 3 | 2 | 1
25202 | kwh import |  |  | float | 3 | 2 | 1
25204 | kvarh lag |  |  | float | 3 | 2 | 1
25206 | kvarh lead |  |  | float | 3 | 2 | 1
25208 | kVAh |  |  | float | 3 | 2 | 1
25210 | energy log this day 01h |  |  | float | 3 | 2 | 4
25218 | energy log this day 02h |  |  | float | 3 | 2 | 4
25226 | energy log this day 03h |  |  | float | 3 | 2 | 4
25234 | energy log this day 04h |  |  | float | 3 | 2 | 4
25242 | energy log this day 05h |  |  | float | 3 | 2 | 4
25250 | energy log this day 06h |  |  | float | 3 | 2 | 4
25258 | energy log this day 07h |  |  | float | 3 | 2 | 4
25266 | energy log this day 08h |  |  | float | 3 | 2 | 4
25274 | energy log this day 09h |  |  | float | 3 | 2 | 4
25282 | energy log this day 10h |  |  | float | 3 | 2 | 4
25290 | energy log this day 11h |  |  | float | 3 | 2 | 4
25298 | energy log this day 12h |  |  | float | 3 | 2 | 4
25306 | energy log this day 13h |  |  | float | 3 | 2 | 4
25314 | energy log this day 14h |  |  | float | 3 | 2 | 4 | 전일 디멘트 로그
25322 | energy log this day 15h |  |  | float | 3 | 2 | 4
25330 | energy log this day 16h |  |  | float | 3 | 2 | 4
25338 | energy log this day 17h |  |  | float | 3 | 2 | 4
25346 | energy log this day 18h |  |  | float | 3 | 2 | 4
25354 | energy log this day 19h |  |  | float | 3 | 2 | 4
25362 | energy log this day 20h |  |  | float | 3 | 2 | 4
25370 | energy log this day 21h |  |  | float | 3 | 2 | 4
25378 | energy log this day 22h |  |  | float | 3 | 2 | 4
25386 | energy log this day 23h |  |  | float | 3 | 2 | 4
25394 |  |  |  | U16 | 3 | 1 | 6
demand log last day
25400 | Time Stamp |  |  | U32 | 3 | 2 | 1
25402 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
25594 |  |  |  | U16 | 3 | 1 | 6
Max/Min last data
25600 | fr |  |  | S16 | 3 | 1 | 1
25601 | re |  |  | S16 | 3 | 1 | 1
25602 | Reset TimeStamp |  |  | UTC | 3 | 2 | 1
25604 | Frequency |  |  | float | 3 | 2 | 4
25612 | Temp |  |  | float | 3 | 2 | 4
25620 | U1 |  |  | float | 3 | 2 | 4
25628 | U2 |  |  | float | 3 | 2 | 4
25636 | U3 |  |  | float | 3 | 2 | 4
25644 | U~ |  |  | float | 3 | 2 | 4
25652 | U12 |  |  | float | 3 | 2 | 4
25660 | U23 |  |  | float | 3 | 2 | 4
25668 | U31 |  |  | float | 3 | 2 | 4
25676 | Upp~ |  |  | float | 3 | 2 | 4
25684 | I1 |  |  | float | 3 | 2 | 4
25692 | I2 |  |  | float | 3 | 2 | 4
25700 | I3 |  |  | float | 3 | 2 | 4
25708 | I~ |  |  | float | 3 | 2 | 4
25716 | I total |  |  | float | 3 | 2 | 4
25724 | In |  |  | float | 3 | 2 | 4
25732 | Isum |  |  | float | 3 | 2 | 4
25740 | P1 |  |  | float | 3 | 2 | 4
25748 | P2 |  |  | float | 3 | 2 | 4
25756 | P3 |  |  | float | 3 | 2 | 4
25764 | P total |  |  | float | 3 | 2 | 4
25772 | Q1 |  |  | float | 3 | 2 | 4
25780 | Q2 |  |  | float | 3 | 2 | 4
25788 | Q3 |  |  | float | 3 | 2 | 4
25796 | Q total |  |  | float | 3 | 2 | 4
25804 | S1 |  |  | float | 3 | 2 | 4
25812 | S2 |  |  | float | 3 | 2 | 4
25820 | S3 |  |  | float | 3 | 2 | 4
25828 | S total |  |  | float | 3 | 2 | 4
25836 | PF L1 |  |  | float | 3 | 2 | 4
25844 | PF L2 |  |  | float | 3 | 2 | 4
25852 | PF L3 |  |  | float | 3 | 2 | 4
25860 | PF total |  |  | float | 3 | 2 | 4
25868 | THD U1 |  |  | float | 3 | 2 | 4
25876 | THD U2 |  |  | float | 3 | 2 | 4
25884 | THD U3 |  |  | float | 3 | 2 | 4
25892 | THD U12 |  |  | float | 3 | 2 | 4
25900 | THD U23 |  |  | float | 3 | 2 | 4
25908 | THD U31 |  |  | float | 3 | 2 | 4
25916 | THD I1 |  |  | float | 3 | 2 | 4
25924 | THD I2 |  |  | float | 3 | 2 | 4
25932 | THD I3 |  |  | float | 3 | 2 | 4
25940 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
25942 | reserved |  |  | U16 | 3 | 1 | 1
25943 | CRC |  |  | U16 | 3 | 1 | 1
25944 |  |  |  | U16 | 3 | 1 | 6
ITIC
25950 | fr |  |  | U16 | 3 | 1 | 1
25951 | re |  |  | U16 | 3 | 1 | 1
25952 | count |  |  | U16 | 3 | 1 | 1
25953 | SEQ |  |  | U16 | 3 | 1 | 1
25954 | Log #1 | start ts |  | UTC | 3 | 2 | 1
25956 |  | start ts(ms) |  | U16 | 3 | 1 | 1
25957 |  | duration |  | U16 | 3 | 1 | 1
25958 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
25959 |  | mask |  | U16 | 3 | 1 | 1
25960 |  | Level 1 |  | float | 3 | 2 | 1
25962 |  | Level 2 |  | float | 3 | 2 | 1
25964 |  | Level 3 |  | float | 3 | 2 | 1
25966 |  | Normal |  | float | 3 | 2 | 1
25968 | Log #2 |  |  | U16 | 3 | 1 | 14
25982 | Log #3 |  |  | U16 | 3 | 1 | 14
25996 | Log #4 |  |  | U16 | 3 | 1 | 14
26010 | Log #5 |  |  | U16 | 3 | 1 | 14
26024 | Log #6 |  |  | U16 | 3 | 1 | 14
26038 | Log #7 |  |  | U16 | 3 | 1 | 14
26052 | Log #8 |  |  | U16 | 3 | 1 | 14
26066 | Log #9 |  |  | U16 | 3 | 1 | 14
26080 | Log #10 |  |  | U16 | 3 | 1 | 14
26094 | Log #11 |  |  | U16 | 3 | 1 | 14
26108 | Log #12 |  |  | U16 | 3 | 1 | 14
26122 | Log #13 |  |  | U16 | 3 | 1 | 14
26136 | Log #14 |  |  | U16 | 3 | 1 | 14
26150 | Log #15 |  |  | U16 | 3 | 1 | 14
26164 | Log #16 |  |  | U16 | 3 | 1 | 14
26178 | Log #17 |  |  | U16 | 3 | 1 | 14
26192 | Log #18 |  |  | U16 | 3 | 1 | 14
26206 | Log #19 |  |  | U16 | 3 | 1 | 14
26220 | Log #20 |  |  | U16 | 3 | 1 | 14
26234 | Log #21 |  |  | U16 | 3 | 1 | 14
26248 | Log #22 |  |  | U16 | 3 | 1 | 14
26262 | Log #23 |  |  | U16 | 3 | 1 | 14
26276 | Log #24 |  |  | U16 | 3 | 1 | 14
26290 | Log #25 |  |  | U16 | 3 | 1 | 14
26304 | Log #26 |  |  | U16 | 3 | 1 | 14
26318 | Log #27 |  |  | U16 | 3 | 1 | 14
26332 | Log #28 |  |  | U16 | 3 | 1 | 14
26346 | Log #29 |  |  | U16 | 3 | 1 | 14
26360 | Log #30 |  |  | U16 | 3 | 1 | 14
26374 | Log #31 |  |  | U16 | 3 | 1 | 14
26388 | Log #32 |  |  | U16 | 3 | 1 | 14
26402 |  |  |  | U16 | 3 | 1 | 8
ITIC(Configurator)
26410 | fr |  |  | U16 | 3 | 1 | 1
26411 | re |  |  | U16 | 3 | 1 | 1
26412 | count |  |  | U16 | 3 | 1 | 1
26413 | reserved |  |  | U16 | 3 | 1 | 1
26414 | Log #1 | start ts |  | UTC | 3 | 2 | 1
26416 |  | start ts(ms) |  | U16 | 3 | 1 | 1
26417 |  | duration |  | U16 | 3 | 1 | 1
26418 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
26419 |  | mask |  | U16 | 3 | 1 | 1
26420 |  | Level 1 |  | float | 3 | 2 | 1
26422 |  | Level 2 |  | float | 3 | 2 | 1
26424 |  | Level 3 |  | float | 3 | 2 | 1
26426 |  | Normal |  | float | 3 | 2 | 1
26428 | Log #2 |  |  | U16 | 3 | 1 | 14
26442 | Log #3 |  |  | U16 | 3 | 1 | 14
26456 | Log #4 |  |  | U16 | 3 | 1 | 14
26470 | Log #5 |  |  | U16 | 3 | 1 | 14
26484 | Log #6 |  |  | U16 | 3 | 1 | 14
26498 | Log #7 |  |  | U16 | 3 | 1 | 14
26512 | Log #8 |  |  | U16 | 3 | 1 | 14
26526 | Log #9 |  |  | U16 | 3 | 1 | 14
26540 | Log #10 |  |  | U16 | 3 | 1 | 14
26554 | Log #11 |  |  | U16 | 3 | 1 | 14
26568 | Log #12 |  |  | U16 | 3 | 1 | 14
26582 | Log #13 |  |  | U16 | 3 | 1 | 14
26596 | Log #14 |  |  | U16 | 3 | 1 | 14
26610 | Log #15 |  |  | U16 | 3 | 1 | 14
26624 | Log #16 |  |  | U16 | 3 | 1 | 14
26638 | Log #17 |  |  | U16 | 3 | 1 | 14
26652 | Log #18 |  |  | U16 | 3 | 1 | 14
26666 | Log #19 |  |  | U16 | 3 | 1 | 14
26680 | Log #20 |  |  | U16 | 3 | 1 | 14
26694 | Log #21 |  |  | U16 | 3 | 1 | 14
26708 | Log #22 |  |  | U16 | 3 | 1 | 14
26722 | Log #23 |  |  | U16 | 3 | 1 | 14
26736 | Log #24 |  |  | U16 | 3 | 1 | 14
26750 | Log #25 |  |  | U16 | 3 | 1 | 14
26764 | Log #26 |  |  | U16 | 3 | 1 | 14
26778 | Log #27 |  |  | U16 | 3 | 1 | 14
26792 | Log #28 |  |  | U16 | 3 | 1 | 14
26806 | Log #29 |  |  | U16 | 3 | 1 | 14
26820 | Log #30 |  |  | U16 | 3 | 1 | 14
26834 | Log #31 |  |  | U16 | 3 | 1 | 14
26848 | Log #32 |  |  | U16 | 3 | 1 | 14
26862 |  |  |  | U16 | 3 | 1 | 8
Setting 영역 시작
PQ Event
26870 | OC Level | 정격의 2배 |  | U16 | 3,16 | 1 | 1
26871 | OC Cycle | unused |  | U16 | 3,16 | 1 | 1
26872 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
26873 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
26874 |  |  |  | U16 | 3,16 | 1 | 2
26876 | Sag Level(%), 90% | < 90% |  | U16 | 3,16 | 1 | 1
26877 | Sag Cycle | unused |  | U16 | 3,16 | 1 | 1
26878 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
26879 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
26880 |  |  |  | U16 | 3,16 | 1 | 2
26882 | Swell Level(%), 110~200~ | > 110% |  | U16 | 3,16 | 1 | 1
26883 | Swell Cycle | unused |  | U16 | 3,16 | 1 | 1
26884 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
26885 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
26886 |  |  |  | U16 | 3,16 | 1 | 2
26888 | Interruption Level, 5% | < 5% |  | U16 | 3,16 | 1 | 1
26889 | Interruption Time, 60s | unused |  | U16 | 3,16 | 1 | 1
26890 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
26891 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
26892 |  |  |  | U16 | 3,16 | 1 | 2
Transient Trigger
26894 | Transient Voltage, HoldOff Time, 20ms | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
26895 | Transient Voltage, Absolute Peak Level, 200% | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
26896 | Transient Voltage, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
26897 | Transient Voltage, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
26898 | Transient Current, HoldOff Time | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
26899 | Transient Current, Absolute Peak Level | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
26900 | Transient Current, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
26901 | Transient Current, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
26902 |  |  |  | U16 | 3,16 | 1 | 12
Recorder
Waveform
26914 | Recorder resolution(32k, 8k) |  |  | U16 | 3,16 | 1 | 1
26915 | Recorded paramater (U or I) |  |  | U16 | 3,16 | 1 | 1
26916 | pre trigger time(0.1s) |  |  | U16 | 3,16 | 1 | 1
26917 | post trigger time(1s) |  |  | U16 | 3,16 | 1 | 1
Disturbance
26918 | Recorder resolution (Half Cycle) |  |  | U16 | 3,16 | 1 | 1
26919 | Recorded parametrs(U or I) |  |  | U16 | 3,16 | 1 | 1
26920 | pre trigger time(100 sample) |  |  | U16 | 3,16 | 1 | 1
26921 | post trigger time(900 sample) |  |  | U16 | 3,16 | 1 | 1
26922 |  |  |  | U16 | 3,16 | 1 | 12
Trend Recorder
26934 | Trend Group #1 Active |  |  | U16 | 3,16 | 1 | 1
26935 | Trend Group #1 Storage Interval |  |  | U16 | 3,16 | 1 | 1
26936 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
26937 | Trend Group #1, Channel #1 |  |  | U16 | 3,16 | 1 | 1
26938 | Trend Group #1, Channel #2 |  |  | U16 | 3,16 | 1 | 1
26939 | Trend Group #1, Channel #3 |  |  | U16 | 3,16 | 1 | 1
26940 | Trend Group #1, Channel #4 |  |  | U16 | 3,16 | 1 | 1
26941 | Trend Group #1, Channel #5 |  |  | U16 | 3,16 | 1 | 1
26942 | Trend Group #1, Channel #6 |  |  | U16 | 3,16 | 1 | 1
26943 | Trend Group #1, Channel #7 |  |  | U16 | 3,16 | 1 | 1
26944 | Trend Group #1, Channel #8 |  |  | U16 | 3,16 | 1 | 1
26945 | Trend Group #1, Channel #9 |  |  | U16 | 3,16 | 1 | 1
26946 | Trend Group #1, Channel #10 |  |  | U16 | 3,16 | 1 | 1
26947 | Trend Group #1, Channel #11 |  |  | U16 | 3,16 | 1 | 1
26948 | Trend Group #1, Channel #12 |  |  | U16 | 3,16 | 1 | 1
26949 | Trend Group #1, Channel #13 |  |  | U16 | 3,16 | 1 | 1
26950 | Trend Group #1, Channel #14 |  |  | U16 | 3,16 | 1 | 1
26951 | Trend Group #1, Channel #15 |  |  | U16 | 3,16 | 1 | 1
26952 | Trend Group #1, Channel #16 |  |  | U16 | 3,16 | 1 | 1
26953 | Trend Group #2 Active |  |  | U16 | 3,16 | 1 | 1
26954 | Trend Group #2 Storage Interval |  |  | U16 | 3,16 | 1 | 1
26955 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
26956 | Trend Group #2, Channel #1 |  |  | U16 | 3,16 | 1 | 1
26957 | Trend Group #2, Channel #2 |  |  | U16 | 3,16 | 1 | 1
26958 | Trend Group #2, Channel #3 |  |  | U16 | 3,16 | 1 | 1
26959 | Trend Group #2, Channel #4 |  |  | U16 | 3,16 | 1 | 1
26960 | Trend Group #2, Channel #5 |  |  | U16 | 3,16 | 1 | 1
26961 | Trend Group #2, Channel #6 |  |  | U16 | 3,16 | 1 | 1
26962 | Trend Group #2, Channel #7 |  |  | U16 | 3,16 | 1 | 1
26963 | Trend Group #2, Channel #8 |  |  | U16 | 3,16 | 1 | 1
26964 | Trend Group #2, Channel #9 |  |  | U16 | 3,16 | 1 | 1
26965 | Trend Group #2, Channel #10 |  |  | U16 | 3,16 | 1 | 1
26966 | Trend Group #2, Channel #11 |  |  | U16 | 3,16 | 1 | 1
26967 | Trend Group #2, Channel #12 |  |  | U16 | 3,16 | 1 | 1
26968 | Trend Group #2, Channel #13 |  |  | U16 | 3,16 | 1 | 1
26969 | Trend Group #2, Channel #14 |  |  | U16 | 3,16 | 1 | 1
26970 | Trend Group #2, Channel #15 |  |  | U16 | 3,16 | 1 | 1
26971 | Trend Group #2, Channel #16 |  |  | U16 | 3,16 | 1 | 1
26972 | Trend Group #3 Active |  |  | U16 | 3,16 | 1 | 1
26973 | Trend Group #3 Storage Interval |  |  | U16 | 3,16 | 1 | 1
26974 |  |  |  | U16 | 3,16 | 1 | 1
26975 | Trend Group #3, Channel #1 |  |  | U16 | 3,16 | 1 | 1
26976 | Trend Group #3, Channel #2 |  |  | U16 | 3,16 | 1 | 1
26977 | Trend Group #3, Channel #3 |  |  | U16 | 3,16 | 1 | 1
26978 | Trend Group #3, Channel #4 |  |  | U16 | 3,16 | 1 | 1
26979 | Trend Group #3, Channel #5 |  |  | U16 | 3,16 | 1 | 1
26980 | Trend Group #3, Channel #6 |  |  | U16 | 3,16 | 1 | 1
26981 | Trend Group #3, Channel #7 |  |  | U16 | 3,16 | 1 | 1
26982 | Trend Group #3, Channel #8 |  |  | U16 | 3,16 | 1 | 1
26983 | Trend Group #3, Channel #9 |  |  | U16 | 3,16 | 1 | 1
26984 | Trend Group #3, Channel #10 |  |  | U16 | 3,16 | 1 | 1
26985 | Trend Group #3, Channel #11 |  |  | U16 | 3,16 | 1 | 1
26986 | Trend Group #3, Channel #12 |  |  | U16 | 3,16 | 1 | 1
26987 | Trend Group #3, Channel #13 |  |  | U16 | 3,16 | 1 | 1
26988 | Trend Group #3, Channel #14 |  |  | U16 | 3,16 | 1 | 1
26989 | Trend Group #3, Channel #15 |  |  | U16 | 3,16 | 1 | 1
26990 | Trend Group #3, Channel #16 |  |  | U16 | 3,16 | 1 | 1
26991 | Trend Group #4 Active |  |  | U16 | 3,16 | 1 | 1
26992 | Trend Group #4 Storage Interval |  |  | U16 | 3,16 | 1 | 1
26993 |  |  |  | U16 | 3,16 | 1 | 1
26994 | Trend Group #4, Channel #1 |  |  | U16 | 3,16 | 1 | 1
26995 | Trend Group #4, Channel #2 |  |  | U16 | 3,16 | 1 | 1
26996 | Trend Group #4, Channel #3 |  |  | U16 | 3,16 | 1 | 1
26997 | Trend Group #4, Channel #4 |  |  | U16 | 3,16 | 1 | 1
26998 | Trend Group #4, Channel #5 |  |  | U16 | 3,16 | 1 | 1
26999 | Trend Group #4, Channel #6 |  |  | U16 | 3,16 | 1 | 1
27000 | Trend Group #4, Channel #7 |  |  | U16 | 3,16 | 1 | 1
27001 | Trend Group #4, Channel #8 |  |  | U16 | 3,16 | 1 | 1
27002 | Trend Group #4, Channel #9 |  |  | U16 | 3,16 | 1 | 1
27003 | Trend Group #4, Channel #10 |  |  | U16 | 3,16 | 1 | 1
27004 | Trend Group #4, Channel #11 |  |  | U16 | 3,16 | 1 | 1
27005 | Trend Group #4, Channel #12 |  |  | U16 | 3,16 | 1 | 1
27006 | Trend Group #4, Channel #13 |  |  | U16 | 3,16 | 1 | 1
27007 | Trend Group #4, Channel #14 |  |  | U16 | 3,16 | 1 | 1
27008 | Trend Group #4, Channel #15 |  |  | U16 | 3,16 | 1 | 1
27009 | Trend Group #4, Channel #16 |  |  | U16 | 3,16 | 1 | 1
27010 |  |  |  | U16 | 3,16 | 1 | 4
Power Quality Report
27014 | Active |  |  | U16 | 3,16 | 1 | 1
27015 | Start Day |  |  | U16 | 3,16 | 1 | 1
27016 |  |  |  | U16 |  | 1 | 8
Alarm Definition
27024 | compare Time Delay(1s) |  |  | U16 | 3,16 | 1 | 1
27025 |  |  |  | U16 |  | 1 | 1
27026 |  |  |  | U16 |  | 1 | 1
27027 |  |  |  | U16 |  | 1 | 1
Alarm Settings
27028 | Alarm Info #1 Channel(0:disabled, >0: enabled) |  |  | U16 | 3,16 | 1 | 1
27029 | Alarm Cond (0: < , 1:>) |  |  | U16 | 3,16 | 1 | 1
27030 | Hysteresis (% of Nominal) |  |  | U16 | 3,16 | 1 | 1
27031 | Alarm Action (None, Relay or Beep) |  |  | U16 | 3,16 | 1 | 1
27032 | Alarm Level |  |  | float | 3,16 | 2 | 1
27034 | Alarm Settings #2 |  |  | U16 | 3,16 | 1 | 6
27040 | Alarm Settings #3 |  |  | U16 | 3,16 | 1 | 6
27046 | Alarm Settings #4 |  |  | U16 | 3,16 | 1 | 6
27052 | Alarm Settings #5 |  |  | U16 | 3,16 | 1 | 6
27058 | Alarm Settings #6 |  |  | U16 | 3,16 | 1 | 6
27064 | Alarm Settings #7 |  |  | U16 | 3,16 | 1 | 6
27070 | Alarm Settings #8 |  |  | U16 | 3,16 | 1 | 6
27076 | Alarm Settings #9 |  |  | U16 | 3,16 | 1 | 6
27082 | Alarm Settings #10 |  |  | U16 | 3,16 | 1 | 6
27088 | Alarm Settings #11 |  |  | U16 | 3,16 | 1 | 6
27094 | Alarm Settings #12 |  |  | U16 | 3,16 | 1 | 6
27100 | Alarm Settings #13 |  |  | U16 | 3,16 | 1 | 6
27106 | Alarm Settings #14 |  |  | U16 | 3,16 | 1 | 6
27112 | Alarm Settings #15 |  |  | U16 | 3,16 | 1 | 6
27118 | Alarm Settings #16 |  |  | U16 | 3,16 | 1 | 6
27124 | Alarm Settings #17 |  |  | U16 | 3,16 | 1 | 6
27130 | Alarm Settings #18 |  |  | U16 | 3,16 | 1 | 6
27136 | Alarm Settings #19 |  |  | U16 | 3,16 | 1 | 6
27142 | Alarm Settings #20 |  |  | U16 | 3,16 | 1 | 6
27148 | Alarm Settings #21 |  |  | U16 | 3,16 | 1 | 6
27154 | Alarm Settings #22 |  |  | U16 | 3,16 | 1 | 6
27160 | Alarm Settings #23 |  |  | U16 | 3,16 | 1 | 6
27166 | Alarm Settings #24 |  |  | U16 | 3,16 | 1 | 6
27172 | Alarm Settings #25 |  |  | U16 | 3,16 | 1 | 6
27178 | Alarm Settings #26 |  |  | U16 | 3,16 | 1 | 6
27184 | Alarm Settings #27 |  |  | U16 | 3,16 | 1 | 6
27190 | Alarm Settings #28 |  |  | U16 | 3,16 | 1 | 6
27196 | Alarm Settings #29 |  |  | U16 | 3,16 | 1 | 6
27202 | Alarm Settings #30 |  |  | U16 | 3,16 | 1 | 6
27208 | Alarm Settings #31 |  |  | U16 | 3,16 | 1 | 6
27214 | Alarm Settings #32 |  |  | U16 | 3,16 | 1 | 6

## Alarm Channel
Trend/Alarm Channel
1 | Temp
2 | Freq
3 | U1
4 | U2
5 | U3
6 | U~
7 | U12
8 | U23
9 | U31
10 | Upp~
11 | Voltage Unbalace, Uo
12 | Voltage Unbalace, Uu
13 | I1
14 | I2
15 | I3
16 | I~
17 | Itotal
18 | In
19 | P1
20 | P2
21 | P3
22 | Ptotal
23 | Q1
24 | Q2
25 | Q3
26 | Qtot
27 | D1
28 | D2
29 | D3
30 | D
31 | S1
32 | S2
33 | S3
34 | Stot
35 | PF1
36 | PF2
37 | PF3
38 | PFtot
39 | THD U1
40 | THD U2
41 | THD U3
42 | THD U12
43 | THD U23
44 | THD U31
45 | THD I1
46 | THD I2
47 | THD I3
48 | Dynamic Demand P+
49 | Dynamic Demand P-
50 | Dynamic Demand Q+
51 | Dynamic Demand Q-
52 | Dynamic Demand S
53 | Dynamic Demand I1
54 | Dynamic Demand I2
55 | Dynamic Demand I3
56 | Max. Demand P+
57 | Max. Demand P=-
58 | Max. Demand Q+
59 | Max. Demand Q-
60 | Max. Demand S
61 | Max. Demand I1
62 | Max. Demand I2
63 | Max. Demand I3
64 | Under Deviation U1
65 | Under Deviation U2
66 | Under Deviation U3
67 | Over Drviation U1
68 | Over Drviation U2
69 | Over Drviation U3
70 | CF U1
71 | CF U2
72 | CF U3
73 | CF U12
74 | CF U23
75 | CF U31
76 | CF I1
77 | CF I2
78 | CF I3
79 | KF I1
80 | KF I2
81 | KF I3
82 | PSt 1
83 | PSt 2
84 | PSt 3
85 | Plt 1
86 | Plt 2
87 | Plt 3
88 | Sig. Volt 1
89 | Sig. Volt 2
90 | Sig. Volt 3