## ToDo&Log
2024-12-18 | 1st draft
2026-06-08 | 3ch redefine
2026-06-08

## #1,2,3 Simple
address | Group | name | Decription | 1P | 3P | Unit | Function code | TYPE | 1P | 3P | Word Count | Item Count
Metering
50000 | Common | Time Stamp |  |  |  |  | 3,4 | U32 |  |  | 2 | 1
50002 |  | Heatbit |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50003 |  | HW Model |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50004 |  | HW Version |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50005 |  | FW Version |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50006 |  | FW_BUILD_YEAR |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50007 |  | FW_BUILD_MON |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50008 |  | FW_BUILD_DAY |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50009 |  | Serial Num |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50010 |  | Status |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50011 |  | reserved |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50012 |  | Internal Temp |  |  |  |  | 3,4 | float |  |  | 2 | 1
50014 |  | reserved |  |  |  |  | 3,4 | U32 |  |  | 2 | 3
50020 | #1 | CB Type |  | ● | ● |  | 3,4 | U16 |  |  | 1 | 1
50021 |  | CB Status |  | ● | ● |  | 3,4 | U16 |  |  | 1 | 1
50022 |  | reserved |  | ● | ● |  | 3,4 | U32 |  |  | 2 | 1
50024 |  | Frequency |  | ● | ● | Hz | 3,4 | float |  |  | 2 | 1
50026 |  | U1 | 상전압 1 | ● | ● | V | 3,4 | float |  |  | 2 | 1
50028 |  | U2 | 상전압 2 |  | ● |  | 3,4 | float |  |  | 2 | 1
50030 |  | U3 | 상전압 3 |  | ● |  | 3,4 | float |  |  | 2 | 1
50032 |  | U12 |  |  | ● |  | 3,4 | float |  |  | 2 | 1
50034 |  | U23 |  |  | ● |  | 3,4 | float |  |  | 2 | 1
50036 |  | U31 |  |  | ● |  | 3,4 | float |  |  | 2 | 1
50038 |  | I1 | 상전류 1 | ● | ● | A | 3,4 | float |  |  | 2 | 1
50040 |  | I2 | 상전류 2 |  | ● |  | 3,4 | float |  |  | 2 | 1
50042 |  | I3 | 상전류 3 |  | ● |  | 3,4 | float |  |  | 2 | 1
50044 |  | In | 누설전류 |  | ● |  | 3,4 | float |  |  | 2 | 1
50046 |  | P1 |  | ● | ● | W | 3,4 | float |  |  | 2 | 1
50048 |  | P2 |  |  | ● |  | 3,4 | float |  |  | 2 | 1
50050 |  | P3 |  |  | ● |  | 3,4 | float |  |  | 2 | 1
50052 |  | P total |  | ● | ● |  | 3,4 | float |  |  | 2 | 1
50054 |  | Q total |  | ● | ● | Var | 3,4 | float |  |  | 2 | 1
50056 |  | S total |  | ● | ● | VA | 3,4 | float |  |  | 2 | 1
50058 |  | PF total |  | ● | ● | % | 3,4 | float |  |  | 2 | 1
50060 |  | kWh_imp |  | ● | ● | kWh | 3,4 | U32 |  |  | 2 | 1
50062 |  | kWh_imp_this_month |  | ● | ● | kWh | 3,4 | U32 |  |  | 2 | 1
50064 |  | kWh_imp_last_month |  | ● | ● | kWh | 3,4 | U32 |  |  | 2 | 1
50066 |  | kVARh_imp |  | ● | ● | kVarh | 3,4 | U32 |  |  | 2 | 1
50068 |  | kVAh |  | ● | ● | kVAh | 3,4 | U32 |  |  | 2 | 1
50070 |  | Volt. Unbalance |  | ● | ● | % | 3,4 | float |  |  | 2 | 1
50072 |  | Current Unbalance |  | ● | ● | % | 3,4 | float |  |  | 2 | 1
50074 |  | THD V1 | 고조파함유율 상전압 1 | ● | ● | % | 3,4 | float |  |  | 2 | 1
50076 |  | THD V2 | 고조파함유율 상전압 2 |  | ● | % | 3,4 | float |  |  | 2 | 1
50078 |  | THD V3 | 고조파함유율 상전압 3 |  | ● | % | 3,4 | float |  |  | 2 | 1
50080 |  | THD I1 | 고조파함유율 상전류 1 | ● | ● | % | 3,4 | float |  |  | 2 | 1
50082 |  | THD I2 | 고조파함유율 상전류 2 |  | ● | % | 3,4 | float |  |  | 2 | 1
50084 |  | THD I3 | 고조파함유율 상전류 3 |  | ● | % | 3,4 | float |  |  | 2 | 1
50086 |  | TDD I1 | 디맨드왜형율 상전류 1 | ● | ● | % | 3,4 | float |  |  | 2 | 1
50088 |  | TDD I2 | 디맨드왜형율 상전류 2 |  | ● | % | 3,4 | float |  |  | 2 | 1
50090 |  | TDD I3 | 디맨드왜형율 상전류 3 |  | ● | % | 3,4 | float |  |  | 2 | 1
50092 |  | reserved |  | ● | ● |  | 3,4 | float |  |  | 2 | 4
50100 | #2 |  |  | ● | ● |  | 3,4 | float |  |  | 1 | 80
50180 | #3 |  |  | ● | ● |  | 3,4 | float |  |  | 1 | 80
50260 | #4 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
50340 | #5 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
50420 | #6 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
50500 | #7 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
50580 | #8 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
50660 | #9 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
Harmonics by order
50740 | #1 | Harmonics V1 | 1~41th | ● | ● |  | 3,4 | S16 |  |  | 1 | 41
50781 |  | Harmonics V2 |  |  | ● |  | 3,4 | S16 |  |  | 1 | 41
50822 |  | Harmonics V3 |  |  | ● |  | 3,4 | S16 |  |  | 1 | 41
50863 |  | Harmonics I1 |  | ● | ● |  | 3,4 | S16 |  |  | 1 | 41
50904 |  | Harmonics I2 |  |  | ● |  | 3,4 | S16 |  |  | 1 | 41
50945 |  | Harmonics I3 |  |  | ● |  | 3,4 | S16 |  |  | 1 | 41
50986 | #2 |  |  | ● | ● | [5 empty] | 1 | 246
51232 | #3 |  |  | ● | ● | [5 empty] | 1 | 246
51478 | #4 |  |  | ● | [6 empty] | 1 | 246
51724 | #5 |  |  | ● | [6 empty] | 1 | 246
51970 | #6 |  |  | ● | [6 empty] | 1 | 246
52216 | #7 |  |  | ● | [6 empty] | 1 | 246
52462 | #8 |  |  | ● | [6 empty] | 1 | 246
52708 | #9 |  |  | ● | [6 empty] | 1 | 246

## common
address | name | 설명 | Unit | TYPE | FC | Word Count | Item Count
IOM Data
6870 | DI status #0 |  |  | U16 | 3 | 1 | 1
6871 | DI status #1 |  |  | U16 | 3 | 1 | 1
6872 | DI status #2 |  |  | U16 | 3 | 1 | 1
6873 | DI status #3 |  |  | U16 | 3 | 1 | 1
6874 | DI Pulse Data #0 |  |  | U32 | 3 | 2 | 1
6876 | DI Pulse Data #1 |  |  | U32 | 3 | 2 | 1
6878 | DI Pulse Data #2 |  |  | U32 | 3 | 2 | 1
6880 | DI Pulse Data #3 |  |  | U32 | 3 | 2 | 1
6882 | TEMP #0 |  |  | float | 3 | 2 | 1
6884 | TEMP #1 |  |  | float | 3 | 2 | 1
6886 | TEMP #2 |  |  | float | 3 | 2 | 1
6888 | TEMP #3 |  |  | float | 3 | 2 | 1
METER INFO
6890 | serial# |  |  | U16 | 3 | 1 | 6
6896 | MAC MSB |  |  | U16 | 3 | 1 | 2
6898 | mac address |  |  | U16 | 3 | 1 | 4
6902 | IP ADDR |  |  | U16 | 3 | 1 | 4
6906 | HW Model |  |  | U16 | 3 | 1 | 1
6907 | HW version |  |  | U16 | 3 | 1 | 1
6908 | FW version |  |  | U16 | 3 | 1 | 1
6909 | FW_BUILD_YEAR |  |  | U16 | 3 | 1 | 1
6910 | FW_BUILD_MON |  |  | U16 | 3 | 1 | 1
6911 | FW_BUILD_DAY |  |  | U16 | 3 | 1 | 1
6912 | HEART BIT |  |  | U16 | 3 | 1 | 1
6913 | MODBUS RX COUNT |  |  | U16 | 3 | 1 | 1
6914 | ALARM STS |  |  | U16 | 3 | 1 | 1
6915 | EVENT STS |  |  | U16 | 3 | 1 | 1
6916 | RSTP STS[0~1] |  |  | U16 | 3 | 1 | 2
6918 | SNTP STS |  |  | U16 | 3 | 1 | 1
6919 | DEV STS |  |  | U16 | 3 | 1 | 1
6920 | NET STS |  |  | U16 | 3 | 1 | 1
6921 | TOT STS |  |  | U16 | 3 | 1 | 1
6922 | reserved |  |  | U16 | 3 | 1 | 8
Communication Settings
6930 | device Id |  |  | U16 | 3,16 | 1 | 1
6931 | Modbus TCP Port |  |  | U16 | 3,16 | 1 | 1
6932 | SNTP Mode | 0 : not use, 1 : use |  | U16 | 3,16 | 1 | 1
6933 | SNTP Interval |  | min | U16 | 3,16 | 1 | 1
6934 | Eth#0 IP |  |  | U16 | 3,16 | 1 | 4
6938 | Eth#0 SUBNET |  |  | U16 | 3,16 | 1 | 4
6942 | Eth#0 GATEWAY |  |  | U16 | 3,16 | 1 | 4
6946 | Eth#0 DNS |  |  | U16 | 3,16 | 1 | 4
6950 | SNTP IP |  |  | U16 | 3,16 | 1 | 4
6954 | Host Name |  |  | U16 | 3,16 | 1 | 16
6970 | DAQ server ip |  |  | U16 | 3,16 | 1 | 4
6974 | DHCP enabled |  |  | U16 | 3,16 | 1 | 1
6975 | DAQ sampling rate (0: 2k, 1: 4k, 2: 8k, 3: 16k, 4: 32k) |  |  | U16 | 3,16 | 1 | 1
6976 | DAQ sampling buffer length (0: 2k, 1: 4k, 2: 8k, 3: 16k, 4: 32k, 5: 64) |  |  | U16 | 3,16 | 1 | 1
6977 | DAQ interval (minute) |  |  | U16 | 3,16 | 1 | 1
6978 | DAQ format |  |  | U16 | 3,16 | 1 | 1
6979 | DAQ device id |  |  | U16 | 3,16 | 1 | 1
6980 | DAQ bitspersample (0: 16bit, 1: 32bit) |  |  | U16 | 3,16 | 1 | 1
6981 | reserved |  |  | U16 | 3,16 | 1 | 9
PT #1~9
6990 | Frequency |  |  | U16 | 3,16 | 1 | 1
6991 | feeder count |  |  | U16 | 3,16 | 1 | 1
6992 | #1 wiring mode | 0: not used 1 : 3p4w 2 : 3p3w(2CT), 3 : 3p3w(3CT) 4: 1p2w(L1), 5 : 1p2w(L2), 6 : 1p2w(L3) 7: 1p3w, 8 : SIMULATION |  | U16 | 3,16 | 1 | 1
6993 | #1 reserved |  |  | U16 | 3,16 | 1 | 1
6994 | #1 V nominal |  |  | U32 | 3,16 | 2 | 1
6996 | #1 PT1 |  |  | U32 | 3,16 | 2 | 1
6998 | #1 PT2 |  |  | U16 | 3,16 | 1 | 1
6999 | #1 reserved |  |  | U16 | 3,16 | 1 | 1
7000 | #2 PT |  |  | U16 | 3,16 | 1 | 8
7008 | #3 PT |  |  | U16 | 3,16 | 1 | 8
7016 | #4 PT |  |  | U16 | 3,16 | 1 | 8
7024 | #5 PT |  |  | U16 | 3,16 | 1 | 8
7032 | #6 PT |  |  | U16 | 3,16 | 1 | 8
7040 | #7 PT |  |  | U16 | 3,16 | 1 | 8
7048 | #8 PT |  |  | U16 | 3,16 | 1 | 8
7056 | #9 PT |  |  | U16 | 3,16 | 1 | 8
CT #1~9
7064 | #1 I Nominal |  |  | U16 | 3,16 | 1 | 1
7065 | #1 CT1 |  |  | U16 | 3,16 | 1 | 1
7066 | #1 CT2 | 0: 5A, 1: 100mA/333mV, 2: Rogowski |  | U16 | 3,16 | 1 | 1
7067 | #1 turns |  |  | U16 | 3,16 | 1 | 1
7068 | #1 Starting Current | (1.0 : 0.002*In, 0.5: 0.001*In) 0 ~ 10000 (단위 : mA) |  | U16 | 3,16 | 1 | 1
7069 | #1 CT1 direction | 0: positive, 1: negative |  | U16 | 3,16 | 1 | 1
7070 | #1 CT2 direction |  |  | U16 | 3,16 | 1 | 1
7071 | #1 CT3 direction |  |  | U16 | 3,16 | 1 | 1
7072 | #1 Rogowski CT Model |  |  | U16 | 3,16 | 1 | 1
7073 | #1 phase offset 1 | * phase resolution 60Hz: 0.0211, 50Hz: 0.0176 * range: +63 ~ -383 1.329 ~ -8.079 1.107 ~ -6.732 |  | U16 | 3,16 | 1 | 1
7074 | #1 phase offset 2 |  |  | U16 | 3,16 | 1 | 1
7075 | #1 phase offset 3 |  |  | U16 | 3,16 | 1 | 1
7076 | #1 ZCT Type | 1: 200mV:100mV 2: 200mV:1.5mA 3: 200mV:0.1mA |  | U16 | 3,16 | 1 | 1
7077 | #1 ZCT Scale |  |  | U16 | 3,16 | 1 | 1
7078 | #1 reserved |  |  | U16 | 3,16 | 1 | 2
7080 | #2 CT |  |  | U16 | 3,16 | 1 | 16
7096 | #3 CT |  |  | U16 | 3,16 | 1 | 16
7112 | #4 CT |  |  | U16 | 3,16 | 1 | 16
7128 | #5 CT |  |  | U16 | 3,16 | 1 | 16
7144 | #6 CT |  |  | U16 | 3,16 | 1 | 16
7160 | #7 CT |  |  | U16 | 3,16 | 1 | 16
7176 | #8 CT |  |  | U16 | 3,16 | 1 | 16
7192 | #9 CT |  |  | U16 | 3,16 | 1 | 16
ETC
7208 | VA type | 0: RMS(S=VA) 1: vector(S=sqrt(P*P+Q*Q) |  | U16 | 3,16 | 1 | 1
7209 | PF sign | 0: IEC, 1: IEEE |  | U16 | 3,16 | 1 | 1
7210 | demand interval |  |  | U16 | 3,16 | 1 | 1
7211 | Max. Demand for current TDD(A) - unused |  |  | U16 | 3,16 | 1 | 1
7212 | Target Demand (W) #1~9 |  |  | U32 | 3,16 | 2 | 9
7230 | backlight off time |  |  | U16 | 3,16 | 1 | 1
7231 | brightness |  |  | U16 | 3,16 | 1 | 1
7232 | auto rotation |  |  | U16 | 3,16 | 1 | 1
7233 | Time Zone (~720 ~ 720) | 분단위 |  | S16 | 3,16 | 1 | 1
7234 | max/min reset period | 0: daily 1: weekly 2: monthly |  | U16 | 3,16 | 1 | 1
7235 | TEST MODE | 0 : not use, 1 : use |  | U16 | 3,16 | 1 | 1
7236 | TEST MODE INTERVAL |  |  | U16 | 3,16 | 1 | 1
7237 |  |  |  | U16 |  | 1 | 1
IOM SETTING
7238 | type |  |  | U16 | 3,16 | 1 | 1
7239 | reserved |  |  | U16 | 3,16 | 1 | 1
7240 | DI TYPE #0~3 | 0 : DI, 1 : PI |  | U16 | 3,16 | 1 | 4
7244 | DI debounce #0~3 | 4~255ms |  | U16 | 3,16 | 1 | 4
7248 | PI Scale #0~3 |  |  | U16 | 3,16 | 1 | 4
7252 | reserved |  |  | U16 | 3,16 | 1 | 14
Command
7266 | UTC Time |  |  | U16 | 3,16 | 1 | 4
7270 |  |  |  | U16 | 3,16 | 1 | 6
7276 | reboot |  |  | U16 | 6 | 1 | 1
7277 | save settings |  |  | U16 | 6 | 1 | 1
7278 | Calibration command all, #1~9 | 0: Enable Calibration 1: U gain 2: I gain 3: W gain 4: Ph gain 5: clear V 6: clear I 7: clear W 8: clear phase 9: IN gain 10: clear IN 11: Disable Calibration 12: save Calibration 13: Upp gain 14: clear Upp gain 15: set dcos 16: clear DcOffset 17: --- 18: --- |  | U16 | 6 | 1 | 10
7288 | V-ref, 1=1V #1~9 |  |  | U16 | 6 | 1 | 1
7289 | I-ref, 1=0.1A #1~9 |  |  | U16 | 6 | 1 | 1
7290 | In-ref, 1=0.1 #1~9 |  |  | U16 | 6 | 1 | 1
7291 | init settings |  |  | U16 | 6 | 1 | 1
7292 | clear PI |  |  | U16 | 6 | 1 | 1
7293 | clear demand ALL,#1~9 |  |  | U16 | 6 | 1 | 10
7303 | clear minmax ALL,#1~9 |  |  | U16 | 6 | 1 | 10
7313 | clear energy ALL,#1~9 |  |  | U16 | 6 | 1 | 10
7323 | clear alarm ALL,#1~9 |  |  | U16 | 6 | 1 | 10
7333 | clear event ALL,#1~9 |  |  | U16 | 6 | 1 | 10
7343 | load event ALL,#1~9 | 1: down, 2:up, 3:top |  | U16 | 6 | 1 | 10
7353 | load alarm ALL,#1~9 | 1: down, 2:up, 3:top |  | U16 | 6 | 1 | 10
7363 | Alarm Ack ALL,#1~9 | not used |  | U16 | 6 | 1 | 10
7373 | Event Ack ALL,#1~9 | not used |  | U16 | 6 | 1 | 10
7383 | load itic #1~3 | 1: down, 2:up, 3:top |  | U16 | 6 | 1 | 3
7386 | load itic2 #1~3 | 1: down, 2:up, 3:top |  | U16 | 6 | 1 | 3
7389 | clear ITIC ALL,#1~3 |  |  | U16 | 6 | 1 | 4
7393 | reserved |  |  | U16 | 6 | 1

## #1CH modbus
address | name | 설명 | Unit | TYPE | FC | Word Count | Item Count
Metering
0 | Time Stamp |  |  | UTC | 3 | 2 | 1
2 | TYPE |  |  | U16 | 3 | 1 | 1
3 | STATUS | 1 : online, 0 : offline |  | U16 | 3 | 1 | 1
4 | Frequency | 라인주파수 | Hz | float | 3 | 2 | 1
6 | Internal Temp |  | ℃ | float | 3 | 2 | 1
8 | U1 | 상전압 1 | V | float | 3 | 2 | 1
10 | U2 | 상전압 2 |  | float | 3 | 2 | 1
12 | U3 | 상전압 3 |  | float | 3 | 2 | 1
14 | U~ | 상전압 평균 |  | float | 3 | 2 | 1
16 | U12 | 선간 전압 12 |  | float | 3 | 2 | 1
18 | U23 | 선간 전압 23 |  | float | 3 | 2 | 1
20 | U31 | 선간 전압 31 |  | float | 3 | 2 | 1
22 | Upp~ | 선간 전압 평균 |  | float | 3 | 2 | 1
24 | Uunbalance2 |  | % | float | 3 | 2 | 1 | Uu=neg/pos*100
26 | Uunbalance0 |  |  | float | 3 | 2 | 1 | Uo=zero/pos*100
28 | U Zero Sequence Mag. |  |  | float | 3 | 2 | 1
30 | U Zero Sequence angle |  |  | float | 3 | 2 | 1
32 | U Positive Sequence Mag. |  |  | float | 3 | 2 | 1
34 | U Positive Sequence angle |  |  | float | 3 | 2 | 1
36 | U Negative Sequence Mag |  |  | float | 3 | 2 | 1
38 | U Negative Sequence angle |  |  | float | 3 | 2 | 1
40 | Angle U1 |  |  | float | 3 | 2 | 1
42 | Angle U2 |  |  | float | 3 | 2 | 1
44 | Angle U3 |  |  | float | 3 | 2 | 1
46 | U Underdeviation L1 |  | % | float | 3 | 2 | 1
48 | U Underdeviation L2 |  | % | float | 3 | 2 | 1
50 | U Underdeviation L3 |  | % | float | 3 | 2 | 1
52 | U Overdeviation L1 |  | % | float | 3 | 2 | 1
54 | U Overdeviation L2 |  | % | float | 3 | 2 | 1
56 | U Overdeviation L3 |  | % | float | 3 | 2 | 1
58 | I1 | 상전류 1 | A | float | 3 | 2 | 1
60 | I2 | 상전류 2 |  | float | 3 | 2 | 1
62 | I3 | 상전류 3 |  | float | 3 | 2 | 1
64 | I~ |  |  | float | 3 | 2 | 1
66 | I total (I1+I2+I3) |  |  | float | 3 | 2 | 1
68 | In(Measured) |  |  | float | 3 | 2 | 1 | 1. 5A: -3P4W(In) -3P3W(Ig), 2. AT/VT: Ig로 사용
70 | In(Calculated) | Ia+Ib+Ic+In = Ig |  | float | 3 | 2 | 1 | 1. 5A: -3P4W(Ig=Ia+Ib+Ic+In), -3P3W(Ig=Ia+Ib+Ic), 2. AT/VT: 5A와 동일
72 | Ig |  |  | float | 3 | 2 | 1
74 | I Zero Sequence Mag |  |  | float | 3 | 2 | 1
76 | I Zero Sequence angle |  |  | float | 3 | 2 | 1
78 | I Positive Sequence Mag. |  |  | float | 3 | 2 | 1
80 | I Positive Sequence angle |  |  | float | 3 | 2 | 1
82 | I Negative Sequence Mag. |  |  | float | 3 | 2 | 1
84 | I Negative Sequence angle |  |  | float | 3 | 2 | 1
86 | Angle I1 |  |  | float | 3 | 2 | 1
88 | Angle I2 |  |  | float | 3 | 2 | 1
90 | Angle I3 |  |  | float | 3 | 2 | 1
92 | Iunbalance2 |  | % | float | 3 | 2 | 1
94 | Iunbalance0 |  |  | float | 3 | 2 | 1
96 | P1 | 유효전력 P1 | W | float | 3 | 2 | 1
98 | P2 | 유효전력 P2 |  | float | 3 | 2 | 1
100 | P3 | 유효전력 P3 |  | float | 3 | 2 | 1
102 | P total | 유효전력 P-total |  | float | 3 | 2 | 1
104 | fP1 |  |  | float | 3 | 2 | 1
106 | fP2 |  |  | float | 3 | 2 | 1
108 | fP3 |  |  | float | 3 | 2 | 1
110 | fP total |  |  | float | 3 | 2 | 1
112 | Q1 | 무효전력 Q1 | VAR | float | 3 | 2 | 1
114 | Q2 | 무효전력 Q2 |  | float | 3 | 2 | 1
116 | Q3 | 무효전력 Q3 |  | float | 3 | 2 | 1
118 | Q total | 무효전력 Q-total |  | float | 3 | 2 | 1
120 | fQ1 |  |  | float | 3 | 2 | 1
122 | fQ2 |  |  | float | 3 | 2 | 1
124 | fQ3 |  |  | float | 3 | 2 | 1
126 | fQ total |  |  | float | 3 | 2 | 1
128 | S1 | 피상전력 S1 | VA | float | 3 | 2 | 1
130 | S2 | 피상전력 S2 |  | float | 3 | 2 | 1
132 | S3 | 피상전력 S3 |  | float | 3 | 2 | 1
134 | S total | 피상전력 S-total |  | float | 3 | 2 | 1
136 | fS1 |  |  | float | 3 | 2 | 1
138 | fS2 |  |  | float | 3 | 2 | 1
140 | fS3 |  |  | float | 3 | 2 | 1
142 | fS total |  |  | float | 3 | 2 | 1
144 | PF1 | 역률 PF1 | % | float | 3 | 2 | 1
146 | PF2 | 역률 PF2 |  | float | 3 | 2 | 1
148 | PF3 | 역률 PF3 |  | float | 3 | 2 | 1
150 | PF total | 역률 PF-total |  | float | 3 | 2 | 1
152 | dPF1 |  | % | float | 3 | 2 | 1
154 | dPF2 |  |  | float | 3 | 2 | 1
156 | dPF3 |  |  | float | 3 | 2 | 1
158 | dPF total |  |  | float | 3 | 2 | 1
160 | deformed Power D L1 |  | W | float | 3 | 2 | 1 | S=sqrt {P^{2}+Q^{2}+D^{2}}
162 | deformed Power D L2 |  |  | float | 3 | 2 | 1
164 | deformed Power D L3 |  |  | float | 3 | 2 | 1
166 | deformed Power D Total |  |  | float | 3 | 2 | 1
168 | Power Angle(atan(fPt,fQt) L1 |  | Degree | float | 3 | 2 | 1 | Angle between fundamental phase voltage and phase current
170 | Power Angle(atan(fPt,fQt) L2 |  |  | float | 3 | 2 | 1
172 | Power Angle(atan(fPt,fQt) L3 |  |  | float | 3 | 2 | 1
174 |  |  |  | float | 3 | 2 | 1
176 | THD V1 |  | % | float | 3 | 2 | 1
178 | THD V2 |  |  | float | 3 | 2 | 1 | Chip에서 제공하는 결과 사용
180 | THD V3 |  |  | float | 3 | 2 | 1
182 | THD V12 |  |  | float | 3 | 2 | 1
184 | THD V23 |  |  | float | 3 | 2 | 1
186 | THD V31 |  |  | float | 3 | 2 | 1
188 | CF V1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
190 | CF V2 |  |  | float | 3 | 2 | 1
192 | CF V3 |  |  | float | 3 | 2 | 1
194 | CF V12 |  |  | float | 3 | 2 | 1
196 | CF V23 |  |  | float | 3 | 2 | 1
198 | CF V31 |  |  | float | 3 | 2 | 1
200 | THD I1 |  |  | float | 3 | 2 | 1
202 | THD I2 |  |  | float | 3 | 2 | 1
204 | THD I3 |  |  | float | 3 | 2 | 1
206 | TDD I1 |  |  | float | 3 | 2 | 1
208 | TDD I2 |  |  | float | 3 | 2 | 1
210 | TDD I3 |  |  | float | 3 | 2 | 1
212 | K I1 | K-FACTOR : 고조파 허용율 |  | float | 3 | 2 | 1
214 | K I2 |  |  | float | 3 | 2 | 1
216 | K I3 |  |  | float | 3 | 2 | 1
218 | CF I1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
220 | CF I2 |  |  | float | 3 | 2 | 1
222 | CF I3 |  |  | float | 3 | 2 | 1
224 | fU1 | 기본파 U1 | V | float | 3 | 2 | 1
226 | fU2 | 기본파 U2 |  | float | 3 | 2 | 1
228 | fU3 | 기본파 U3 |  | float | 3 | 2 | 1
230 | fU~ | 기본파 전압 평균 |  | float | 3 | 2 | 1
232 | fI1 | 기본파 I1 | A | float | 3 | 2 | 1
234 | fI2 | 기본파 I2 |  | float | 3 | 2 | 1
236 | fI3 | 기본파 I3 |  | float | 3 | 2 | 1
238 | fI~ | 기본파 전류 평균 |  | float | 3 | 2 | 1
Energy
240 | import kwh(0 ~ 999,999,999.9 kw) | 누적 유효전력량 |  | U32 | 3 | 2 | 1
242 | export kwh |  |  | U32 | 3 | 2 | 1
244 | import kvarh |  |  | U32 | 3 | 2 | 1
246 | export kvarh |  |  | U32 | 3 | 2 | 1
248 | kvah |  |  | U32 | 3 | 2 | 1
250 |  |  |  | U32 | 3 | 2 | 1
252 | import kwh this month |  |  | U32 | 3 | 2 | 1
254 | export kwh this month |  |  | U32 | 3 | 2 | 1
256 | import kvarh this month |  |  | U32 | 3 | 2 | 1
258 | export kvarh this month |  |  | U32 | 3 | 2 | 1
260 | kvah this month |  |  | U32 | 3 | 2 | 1
262 |  |  |  | U32 | 3 | 2 | 1
264 | import kwh last month |  |  | U32 | 3 | 2 | 1 | Demand P(import)
266 | export kwh last month |  |  | U32 | 3 | 2 | 1
268 | import kvarh last month |  |  | U32 | 3 | 2 | 1
270 | export kvarh last month |  |  | U32 | 3 | 2 | 1
272 | kvah last month |  |  | U32 | 3 | 2 | 1
274 |  |  |  | U32 | 3 | 2 | 1
276 | import kwh | 0~999,999,999.999 kw |  | U64 | 3 | 4 | 1 | Demand P(import)
280 | export kwh |  |  | U64 | 3 | 4 | 1
284 | import kvarh |  |  | U64 | 3 | 4 | 1
288 | export kvarh |  |  | U64 | 3 | 4 | 1
292 | kvah |  |  | U64 | 3 | 4 | 1
296 |  |  |  | U64 | 3 | 4 | 1
Demand
300 | Time Stamp |  |  | UTC | 3 | 2 | 1
302 | Max Demand P(import) |  |  | float | 3 | 2 | 1
304 | Time Stamp |  |  | UTC | 3 | 2 | 1
306 | Max Demand P(export) |  |  | float | 3 | 2 | 1
308 | Time Stamp |  |  | UTC | 3 | 2 | 1
310 | Max Demand Q(import) |  |  | float | 3 | 2 | 1
312 | Time Stamp |  |  | UTC | 3 | 2 | 1
314 | Max Demand Q(export) |  |  | float | 3 | 2 | 1
316 | Time Stamp |  |  | UTC | 3 | 2 | 1
318 | Max Demand S |  |  | float | 3 | 2 | 1
320 | Time Stamp |  |  | UTC | 3 | 2 | 1
322 | Max Demand I1 |  |  | float | 3 | 2 | 1
324 | Time Stamp |  |  | UTC | 3 | 2 | 1
326 | Max Demand I2 |  |  | float | 3 | 2 | 1
328 | Time Stamp |  |  | UTC | 3 | 2 | 1
330 | Max Demand I3 |  |  | float | 3 | 2 | 1
332 | Demand time stamp |  |  | UTC | 3 | 2 | 1
334 | Demand P(import) |  |  | float | 3 | 2 | 1
336 | Demand P(export) |  |  | float | 3 | 2 | 1 | 최근 24시간 그래프 그린다
338 | Demand Q(import) |  |  | float | 3 | 2 | 1
340 | Demand Q(export) |  |  | float | 3 | 2 | 1
342 | Demand S(export) |  |  | float | 3 | 2 | 1
344 | Demand I1 |  |  | float | 3 | 2 | 1
346 | Demand I2 |  |  | float | 3 | 2 | 1
348 | Demand I3 |  |  | float | 3 | 2 | 1
350 | Present Demand P(import) |  |  | float | 3 | 2 | 1
352 | Present Demand P(export) |  |  | float | 3 | 2 | 1
354 | Present Demand Q(import) |  |  | float | 3 | 2 | 1
356 | Present Demand Q(export) |  |  | float | 3 | 2 | 1
358 | Present Demand S(export) |  |  | float | 3 | 2 | 1
360 | Forecast Demand P(export) |  |  | float | 3 | 2 | 1
362 | Demand P 15m(import) |  |  | float | 3 | 2 | 1
364 |  |  |  | float | 3 | 2 | 1
366 |  |  |  | float | 3 | 2 | 1
368 | Time Stamp(Demand Log 시작일) |  |  | U32 | 3 | 2 | 1
370 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
562 |  |  |  | float | 3 | 2 | 19
Voltage Quality RealTime Value
600 | Voltage Under Deviation L1 |  | % | float | 3 | 2 | 1
602 | Voltage Under Deviation L2 |  | % | float | 3 | 2 | 1
604 | Voltage Under Deviation L3 |  | % | float | 3 | 2 | 1
606 | Voltage Under Value L1 |  | rms | float | 3 | 2 | 1
608 | Voltage Under Value L2 |  | rms | float | 3 | 2 | 1
610 | Voltage Under Value L3 |  | rms | float | 3 | 2 | 1
612 | Voltage Over Deviation L1 |  | % | float | 3 | 2 | 1
614 | Voltage Over Deviation L2 |  | % | float | 3 | 2 | 1
616 | Voltage Over Deviation L3 |  | % | float | 3 | 2 | 1
618 | Voltage Over Value L1 |  | rms | float | 3 | 2 | 1
620 | Voltage Over Value L2 |  | rms | float | 3 | 2 | 1
622 | Voltage Over Value L3 |  | rms | float | 3 | 2 | 1
624 | Flickers Pi L1 | 150/180 Cycles |  | float | 3 | 2 | 1
626 | Flickers Pi L2 |  |  | float | 3 | 2 | 1
628 | Flickers Pi L3 |  |  | float | 3 | 2 | 1
630 | Flicker Pst L1 | 10min |  | float | 3 | 2 | 1
632 | Flicker Pst L2 |  |  | float | 3 | 2 | 1
634 | Flicker Pst L3 |  |  | float | 3 | 2 | 1
636 | Flicker Plt L1 | 2hr |  | float | 3 | 2 | 1 | 최근 24시간 그래프 그린다
638 | Flicker Plt L2 |  |  | float | 3 | 2 | 1
640 | Flicker Plt L3 |  |  | float | 3 | 2 | 1
642 | Signaling Volt L1 | Magnitude of current 10/12 cycles as a percentage of nominal voltage. |  | float | 3 | 2 | 1
644 | Signaling Volt L2 |  |  | float | 3 | 2 | 1
646 | Signaling Volt L3 |  |  | float | 3 | 2 | 1
648 | Signaling Volt Max L1 | Maximum magnitude of MSV from recording started as a percentage of nominal voltage |  | float | 3 | 2 | 1
650 | Signaling Volt Max L2 |  |  | float | 3 | 2 | 1
652 | Signaling Volt Max L3 |  |  | float | 3 | 2 | 1
654 |  |  |  | float | 3 | 2 | 23
EN50160 This Week
700 | start date |  |  | UTC | 3 | 2 | 1
702 | end date |  |  | UTC | 3 | 2 | 1
704 | status&compliance | bit 0: Freq Var1 bit 1: Freq Var2 bit 2: Volt Var1 L1 bit 3: Volt Var1 L2 bit 4: Volt Var1 L3 bit 5: Volt Var2 L1 bit 6: Volt Var2 L2 bit 7: Volt Var2 L3 bit 8: Unbalance bit 9: Volt THD L1 bit 10: Volt THD L2 bit 11: Volt THD L3 bit 12: Volt HD L1 bit 13: Volt HD L2 bit 14: Volt HD L3 bit 15: Pst L1 bit 16: Pst L2 bit 17: Pst L3 bit 18: Plt L1 bit 19: Plt L2 bit 20: Plt L3 bit 21: SigVolt L1 bit 22: SigVolt L2 bit 23: SigVolt L3 bit 31: Complete [status] 0: OK 1: failed |  | U32 | 3 | 2 | 1
706 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1 | 95%/Week
707 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1 | Info Only
708 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
709 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
710 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
711 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
712 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
713 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1 | Info Only
714 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
715 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
716 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
717 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
718 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
719 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
720 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
721 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
722 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
723 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
724 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
725 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
726 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
727 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
728 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
729 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
730 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
731 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1 | 99%/Day
732 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
733 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
734 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
735 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
736 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
737 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
738 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
739 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
740 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
741 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
742 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
743 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
744 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
745 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
746 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
747 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
748 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
749 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
EN50160 Last Week
750 | start date |  |  | UTC | 3 | 2 | 1
752 | end date |  |  | UTC | 3 | 2 | 1
754 | status |  |  | U16 | 3 | 1 | 1
755 | compilance |  |  | U16 | 3 | 1 | 1
756 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1
757 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1
758 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
759 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
760 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1
761 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
762 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
763 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1
764 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
765 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
766 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1
767 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
768 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
769 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1
770 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
771 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
772 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1
773 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
774 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
775 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1
776 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
777 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
778 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1
779 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
780 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
781 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1
782 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
783 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
784 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
785 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
786 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
787 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
788 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
789 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
790 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
791 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
792 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
793 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
794 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
795 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
796 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
797 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
798 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
799 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
Harmonics
800 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
864 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
928 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
992 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
1056 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
1120 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
1184 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
1248 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
1312 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
1376 |  |  |  | S16 | 3 | 1 | 24
Inter Harmonics
1400 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
1464 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
1528 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
1592 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
1656 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
1720 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
1784 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
1848 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
1912 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
1976 |  |  |  | S16 | 3 | 1 | 24
Max/Min
2000 | fr |  |  | U16 | 3 | 1 | 1
2001 | re |  |  | U16 | 3 | 1 | 1
2002 | Reset TimeStamp |  |  | UTC | 3 | 2 | 1
2004 | Frequency | Max |  | float | 3 | 2 | 1
2006 |  | Max Timestamp |  | UTC | 3 | 2 | 1
2008 |  | Min |  | float | 3 | 2 | 1
2010 |  | Min Timestamp |  | UTC | 3 | 2 | 1
2012 | Temp |  |  | float | 3 | 2 | 4
2020 | U1 |  |  | float | 3 | 2 | 4
2028 | U2 |  |  | float | 3 | 2 | 4
2036 | U3 |  |  | float | 3 | 2 | 4 | http://www.relaytech.com/symcomp_calculator.htm
2044 | U~ |  |  | float | 3 | 2 | 4
2052 | U12 |  |  | float | 3 | 2 | 4
2060 | U23 |  |  | float | 3 | 2 | 4
2068 | U31 |  |  | float | 3 | 2 | 4
2076 | Upp~ |  |  | float | 3 | 2 | 4
2084 | I1 |  |  | float | 3 | 2 | 4
2092 | I2 |  |  | float | 3 | 2 | 4
2100 | I3 |  |  | float | 3 | 2 | 4
2108 | I~ |  |  | float | 3 | 2 | 4
2116 | I total |  |  | float | 3 | 2 | 4
2124 | In |  |  | float | 3 | 2 | 4
2132 | Isum |  |  | float | 3 | 2 | 4
2140 | P1 |  |  | float | 3 | 2 | 4
2148 | P2 |  |  | float | 3 | 2 | 4
2156 | P3 |  |  | float | 3 | 2 | 4
2164 | P total |  |  | float | 3 | 2 | 4
2172 | Q1 |  |  | float | 3 | 2 | 4
2180 | Q2 |  |  | float | 3 | 2 | 4
2188 | Q3 |  |  | float | 3 | 2 | 4
2196 | Q total |  |  | float | 3 | 2 | 4
2204 | S1 |  |  | float | 3 | 2 | 4
2212 | S2 |  |  | float | 3 | 2 | 4
2220 | S3 |  |  | float | 3 | 2 | 4
2228 | S total |  |  | float | 3 | 2 | 4
2236 | PF L1 |  |  | float | 3 | 2 | 4
2244 | PF L2 |  |  | float | 3 | 2 | 4
2252 | PF L3 |  |  | float | 3 | 2 | 4
2260 | PF total |  |  | float | 3 | 2 | 4
2268 | THD U1 |  |  | float | 3 | 2 | 4
2276 | THD U2 |  |  | float | 3 | 2 | 4
2284 | THD U3 |  |  | float | 3 | 2 | 4
2292 | THD U12 |  |  | float | 3 | 2 | 4
2300 | THD U23 |  |  | float | 3 | 2 | 4
2308 | THD U31 |  |  | float | 3 | 2 | 4
2316 | THD I1 |  |  | float | 3 | 2 | 4
2324 | THD I2 |  |  | float | 3 | 2 | 4
2332 | THD I3 |  |  | float | 3 | 2 | 4
2340 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
2342 | reserved |  |  | U16 | 3 | 1 | 1
2343 | CRC |  |  | U16 | 3 | 1 | 1
2344 |  |  |  | U16 | 3 | 1 | 6
alarm status
2350 | fr |  |  | U16 | 3 | 1 | 1
2351 | re |  |  | U16 | 3 | 1 | 1
2352 | reset Ts |  |  | UTC | 3 | 2 | 1
2354 | Alarm State #1 | Alarm Channel |  | U16 | 3 | 1 | 1
2355 |  | Alarm Condition |  | U16 | 3 | 1 | 1
2356 |  | Alarm Level |  | float | 3 | 2 | 1
2358 |  | Alarm Status |  | U16 | 3 | 1 | 1
2359 |  | Alarm Count |  | U16 | 3 | 1 | 1
2360 | Alarm State #2 |  |  | U16 | 3 | 1 | 6
2366 | Alarm State #3 |  |  | U16 | 3 | 1 | 6
2372 | Alarm State #4 |  |  | U16 | 3 | 1 | 6
2378 | Alarm State #5 |  |  | U16 | 3 | 1 | 6
2384 | Alarm State #6 |  |  | U16 | 3 | 1 | 6
2390 | Alarm State #7 |  |  | U16 | 3 | 1 | 6
2396 | Alarm State #8 |  |  | U16 | 3 | 1 | 6
2402 | Alarm State #9 |  |  | U16 | 3 | 1 | 6
2408 | Alarm State #10 |  |  | U16 | 3 | 1 | 6
2414 | Alarm State #11 |  |  | U16 | 3 | 1 | 6
2420 | Alarm State #12 |  |  | U16 | 3 | 1 | 6
2426 | Alarm State #13 |  |  | U16 | 3 | 1 | 6
2432 | Alarm State #14 |  |  | U16 | 3 | 1 | 6
2438 | Alarm State #15 |  |  | U16 | 3 | 1 | 6
2444 | Alarm State #16 |  |  | U16 | 3 | 1 | 6
2450 | Alarm State #17 |  |  | U16 | 3 | 1 | 6
2456 | Alarm State #18 |  |  | U16 | 3 | 1 | 6
2462 | Alarm State #19 |  |  | U16 | 3 | 1 | 6
2468 | Alarm State #20 |  |  | U16 | 3 | 1 | 6
2474 | Alarm State #21 |  |  | U16 | 3 | 1 | 6
2480 | Alarm State #22 |  |  | U16 | 3 | 1 | 6
2486 | Alarm State #23 |  |  | U16 | 3 | 1 | 6
2492 | Alarm State #24 |  |  | U16 | 3 | 1 | 6
2498 | Alarm State #25 |  |  | U16 | 3 | 1 | 6
2504 | Alarm State #26 |  |  | U16 | 3 | 1 | 6
2510 | Alarm State #27 |  |  | U16 | 3 | 1 | 6
2516 | Alarm State #28 |  |  | U16 | 3 | 1 | 6
2522 | Alarm State #29 |  |  | U16 | 3 | 1 | 6
2528 | Alarm State #30 |  |  | U16 | 3 | 1 | 6
2534 | Alarm State #31 |  |  | U16 | 3 | 1 | 6
2540 | Alarm State #32 |  |  | U16 | 3 | 1 | 6
2546 | update Ts |  |  | U32 | 3 | 2 | 1
2548 | Global Alarm Status | (alarm 하나라도 있으면 1, 아니면 0) |  | U16 | 3 | 1 | 1
2549 |  |  |  | U16 | 3 | 1 | 1
alarm log
2550 | fr | 0 ~ 1023 |  | U16 | 3 | 1 | 1
2551 | re | 0 ~ 1023 |  | U16 | 3 | 1 | 1
2552 | count | 전체 log 수 |  | U16 | 3 | 1 | 1
2553 | seq |  |  | U16 | 3 | 1 | 1
2554 | Alarm Log #1 | Time Stamp |  | UTC | 3 | 2 | 1 | 2019-5-11변경
2556 |  | status |  | U16 | 3 | 1 | 1
2557 |  | Alarm Channel & Condition |  | U16 | 3 | 1 | 1
2558 |  | level |  | float | 3 | 2 | 1
2560 |  | Value |  | float | 3 | 2 | 1
2562 | Alarm Log #2 |  |  | U16 | 3 | 1 | 8
2570 | Alarm Log #3 |  |  | U16 | 3 | 1 | 8
2578 | Alarm Log #4 |  |  | U16 | 3 | 1 | 8
2586 | Alarm Log #5 |  |  | U16 | 3 | 1 | 8
2594 | Alarm Log #6 |  |  | U16 | 3 | 1 | 8
2602 | Alarm Log #7 |  |  | U16 | 3 | 1 | 8
2610 | Alarm Log #8 |  |  | U16 | 3 | 1 | 8
2618 | Alarm Log #9 |  |  | U16 | 3 | 1 | 8
2626 | Alarm Log #10 |  |  | U16 | 3 | 1 | 8
2634 | Alarm Log #11 |  |  | U16 | 3 | 1 | 8
2642 | Alarm Log #12 |  |  | U16 | 3 | 1 | 8
2650 | Alarm Log #13 |  |  | U16 | 3 | 1 | 8
2658 | Alarm Log #14 |  |  | U16 | 3 | 1 | 8
2666 | Alarm Log #15 |  |  | U16 | 3 | 1 | 8
2674 | Alarm Log #16 |  |  | U16 | 3 | 1 | 8
2682 | Alarm Log #17 |  |  | U16 | 3 | 1 | 8
2690 | Alarm Log #18 |  |  | U16 | 3 | 1 | 8
2698 | Alarm Log #19 |  |  | U16 | 3 | 1 | 8
2706 | Alarm Log #20 |  |  | U16 | 3 | 1 | 8
2714 | Alarm Log #21 |  |  | U16 | 3 | 1 | 8
2722 | Alarm Log #22 |  |  | U16 | 3 | 1 | 8
2730 | Alarm Log #23 |  |  | U16 | 3 | 1 | 8
2738 | Alarm Log #24 |  |  | U16 | 3 | 1 | 8
2746 | Alarm Log #25 |  |  | U16 | 3 | 1 | 8
2754 | Alarm Log #26 |  |  | U16 | 3 | 1 | 8
2762 | Alarm Log #27 |  |  | U16 | 3 | 1 | 8
2770 | Alarm Log #28 |  |  | U16 | 3 | 1 | 8
2778 | Alarm Log #29 |  |  | U16 | 3 | 1 | 8
2786 | Alarm Log #30 |  |  | U16 | 3 | 1 | 8
2794 | Alarm Log #31 |  |  | U16 | 3 | 1 | 8
2802 | Alarm Log #32 |  |  | U16 | 3 | 1 | 8
2810 |  |  |  | U16 | 3 | 1 | 40
이벤트 리스트
2850 | fr | 0 ~ 1023 |  | U16 | 3 | 1 | 1
2851 | re | 0 ~ 1023 |  | U16 | 3 | 1 | 1
2852 | count | 0 ~ 1023 |  | U16 | 3 | 1 | 1
2853 | seq |  |  | U16 | 3 | 1 | 1
PQ 이벤트(Sag, Swell, Transient, OC)
2854 | start ts |  |  | UTC | 3 | 2 | 1
2856 | start ts(ms) |  |  | U16 | 3 | 1 | 1
2857 | duration |  |  | U16 | 3 | 1 | 1
2858 | type | 1 : E_SAG 2 : E_SWELL 3 : E_sINTR 4 : E_lINTR 5 : E_OC 6 : E_RVC 7 : E_TrV 8 : E_TrC |  | U16 | 3 | 1 | 1
2859 | mask |  |  | U16 | 3 | 1 | 1
2860 | Level 1 |  |  | float | 3 | 2 | 1
2862 | Level 2 |  |  | float | 3 | 2 | 1
2864 | Level 3 |  |  | float | 3 | 2 | 1
2866 | PQ Event #2 |  |  | U16 | 3 | 1 | 12
2878 | PQ Event #3 |  |  | U16 | 3 | 1 | 12
2890 | PQ Event #4 |  |  | U16 | 3 | 1 | 12
2902 | PQ Event #5 |  |  | U16 | 3 | 1 | 12
2914 | PQ Event #6 |  |  | U16 | 3 | 1 | 12
2926 | PQ Event #7 |  |  | U16 | 3 | 1 | 12
2938 | PQ Event #8 |  |  | U16 | 3 | 1 | 12
2950 | PQ Event #9 |  |  | U16 | 3 | 1 | 12
2962 | PQ Event #10 |  |  | U16 | 3 | 1 | 12
2974 | PQ Event #11 |  |  | U16 | 3 | 1 | 12
2986 | PQ Event #12 |  |  | U16 | 3 | 1 | 12
2998 | PQ Event #13 |  |  | U16 | 3 | 1 | 12
3010 | PQ Event #14 |  |  | U16 | 3 | 1 | 12
3022 | PQ Event #15 |  |  | U16 | 3 | 1 | 12
3034 | PQ Event #16 |  |  | U16 | 3 | 1 | 12
3046 | PQ Event #17 |  |  | U16 | 3 | 1 | 12
3058 | PQ Event #18 |  |  | U16 | 3 | 1 | 12
3070 | PQ Event #19 |  |  | U16 | 3 | 1 | 12
3082 | PQ Event #20 |  |  | U16 | 3 | 1 | 12
3094 | PQ Event #21 |  |  | U16 | 3 | 1 | 12
3106 | PQ Event #22 |  |  | U16 | 3 | 1 | 12
3118 | PQ Event #23 |  |  | U16 | 3 | 1 | 12
3130 | PQ Event #24 |  |  | U16 | 3 | 1 | 12
3142 | PQ Event #25 |  |  | U16 | 3 | 1 | 12
3154 | PQ Event #26 |  |  | U16 | 3 | 1 | 12
3166 | PQ Event #27 |  |  | U16 | 3 | 1 | 12
3178 | PQ Event #28 |  |  | U16 | 3 | 1 | 12
3190 | PQ Event #29 |  |  | U16 | 3 | 1 | 12
3202 | PQ Event #30 |  |  | U16 | 3 | 1 | 12
3214 | PQ Event #31 |  |  | U16 | 3 | 1 | 12
3226 | PQ Event #32 |  |  | U16 | 3 | 1 | 12
3238 |  |  |  | U16 | 3 | 1 | 2
PQ Event Counter
3240 |  |  |  | U16 | 3 | 1 | 1
3241 |  |  |  | U16 | 3 | 1 | 1
3242 |  |  |  | U16 | 3 | 1 | 1
3243 | Sag Coount |  |  | U16 | 3 | 1 | 1
3244 | Swell Count |  |  | U16 | 3 | 1 | 1
3245 |  |  |  | U16 | 3 | 1 | 1
3246 |  |  |  | U16 | 3 | 1 | 1
3247 |  |  |  | U16 | 3 | 1 | 1
3248 |  |  |  | U16 | 3 | 1 | 1
3249 |  |  |  | U16 | 3 | 1 | 1
Wave Sample | [7 empty] | 32K: 67,107,786 8K: 74,518,668 첫번째 번지 접근시 wave data를 modbus map으로 load 한다
3250 | Wave Form V1 (160 sample) |  |  | S16 | 3 | 1 | 160
3410 | Wave Form V2 (160 sample) |  |  | S16 | 3 | 1 | 160
3570 | Wave Form V3 (160 sample) |  |  | S16 | 3 | 1 | 160
3730 | Wave Form V12 (160 sample) |  |  | S16 | 3 | 1 | 160
3890 | Wave Form V23 (160 sample) |  |  | S16 | 3 | 1 | 160
4050 | Wave Form V31 (160 sample) |  |  | S16 | 3 | 1 | 160
4210 | Wave Form I1 (160 sample) |  |  | S16 | 3 | 1 | 160
4370 | Wave Form I2 (160 sample) |  |  | S16 | 3 | 1 | 160
4530 | Wave Form I3 (160 sample) |  |  | S16 | 3 | 1 | 160
4690 | vscale |  |  | float | 3 | 2 | 1
4692 | iscale |  |  | float | 3 | 2 | 1
4694 |  |  |  | S16 | 3 | 1 | 6
월간리포트 생성위한 10분 평균
4700 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
4702 | U1 |  |  | float | 3 | 2 | 1
4704 | U2 |  |  | float | 3 | 2 | 1
4706 | U3 |  |  | float | 3 | 2 | 1
4708 | U THD1 |  |  | float | 3 | 2 | 1
4710 | U THD2 |  |  | float | 3 | 2 | 1
4712 | U THD3 |  |  | float | 3 | 2 | 1
4714 | Upp THD1 |  |  | float | 3 | 2 | 1
4716 | Upp THD2 |  |  | float | 3 | 2 | 1
4718 | Upp THD3 |  |  | float | 3 | 2 | 1
4720 | U Unbal Uu |  |  | float | 3 | 2 | 1
4722 | U Unbal Uo |  |  | float | 3 | 2 | 1
4724 | I1 |  |  | float | 3 | 2 | 1
4726 | I2 |  |  | float | 3 | 2 | 1
4728 | I3 |  |  | float | 3 | 2 | 1
4730 | In |  |  | float | 3 | 2 | 1
4732 | I THD1 |  |  | float | 3 | 2 | 1
4734 | I THD2 |  |  | float | 3 | 2 | 1
4736 | I THD3 |  |  | float | 3 | 2 | 1
4738 | I TDD1 |  |  | float | 3 | 2 | 1
4740 | I TDD2 |  |  | float | 3 | 2 | 1
4742 | I TDD3 |  |  | float | 3 | 2 | 1
4744 | K-factor 1 |  |  | float | 3 | 2 | 1
4746 | K-factor 2 |  |  | float | 3 | 2 | 1
4748 | K-factor 3 |  |  | float | 3 | 2 | 1
4750 | I Unbal Iu |  |  | float | 3 | 2 | 1
4752 | I Unbal Io |  |  | float | 3 | 2 | 1
4754 | kw imp |  |  | float | 3 | 2 | 1
4756 | kw exp |  |  | float | 3 | 2 | 1
4758 | kvar lag |  |  | float | 3 | 2 | 1
4760 | kvar lead |  |  | float | 3 | 2 | 1
4762 | kVA |  |  | float | 3 | 2 | 1
4764 | PF |  |  | float | 3 | 2 | 1
4766 | dPF |  |  | float | 3 | 2 | 1
4768 | temperature #1 |  |  | float | 3 | 2 | 1
4770 | temperature #2 |  |  | float | 3 | 2 | 1
4772 | temperature #3 |  |  | float | 3 | 2 | 1
4774 | temperature #4 |  |  | float | 3 | 2 | 1
4776 | temperature #5 |  |  | float | 3 | 2 | 1 | *통신이 끊어진 경우 복구를 위해 사용된다
4778 | Harmonics V1 |  |  | S16 | 3 | 1 | 24
4802 | Harmonics V2 |  |  | S16 | 3 | 1 | 24 | demand
4826 | Harmonics V3 |  |  | S16 | 3 | 1 | 24
4850 | Harmonics V12 |  |  | S16 | 3 | 1 | 24
4874 | Harmonics V23 |  |  | S16 | 3 | 1 | 24
4898 | Harmonics V31 |  |  | S16 | 3 | 1 | 24
4922 | Harmonics I1 |  |  | S16 | 3 | 1 | 24
4946 | Harmonics I2 |  |  | S16 | 3 | 1 | 24
4970 | Harmonics I3 |  |  | S16 | 3 | 1 | 24
4994 |  |  |  | U16 | 3 | 1 | 6
Energy log
5000 | Time Stamp |  |  | UTC | 3 | 2 | 1
5002 | kwh import |  |  | float | 3 | 2 | 1
5004 | kvarh lag |  |  | float | 3 | 2 | 1
5006 | kvarh lead |  |  | float | 3 | 2 | 1
5008 | kVAh |  |  | float | 3 | 2 | 1
5010 | energy log last day 01h |  |  | float | 3 | 2 | 4
5018 | energy log last day 02h |  |  | float | 3 | 2 | 4
5026 | energy log last day 03h |  |  | float | 3 | 2 | 4
5034 | energy log last day 04h |  |  | float | 3 | 2 | 4
5042 | energy log last day 05h |  |  | float | 3 | 2 | 4
5050 | energy log last day 06h |  |  | float | 3 | 2 | 4
5058 | energy log last day 07h |  |  | float | 3 | 2 | 4
5066 | energy log last day 08h |  |  | float | 3 | 2 | 4
5074 | energy log last day 09h |  |  | float | 3 | 2 | 4
5082 | energy log last day 10h |  |  | float | 3 | 2 | 4
5090 | energy log last day 11h |  |  | float | 3 | 2 | 4
5098 | energy log last day 12h |  |  | float | 3 | 2 | 4
5106 | energy log last day 13h |  |  | float | 3 | 2 | 4
5114 | energy log last day 14h |  |  | float | 3 | 2 | 4
5122 | energy log last day 15h |  |  | float | 3 | 2 | 4
5130 | energy log last day 16h |  |  | float | 3 | 2 | 4
5138 | energy log last day 17h |  |  | float | 3 | 2 | 4
5146 | energy log last day 18h |  |  | float | 3 | 2 | 4
5154 | energy log last day 19h |  |  | float | 3 | 2 | 4
5162 | energy log last day 20h |  |  | float | 3 | 2 | 4
5170 | energy log last day 21h |  |  | float | 3 | 2 | 4
5178 | energy log last day 22h |  |  | float | 3 | 2 | 4
5186 | energy log last day 23h |  |  | float | 3 | 2 | 4
5194 |  |  |  | U16 | 3 | 1 | 6
5200 | Time Stamp |  |  | UTC | 3 | 2 | 1
5202 | kwh import |  |  | float | 3 | 2 | 1
5204 | kvarh lag |  |  | float | 3 | 2 | 1
5206 | kvarh lead |  |  | float | 3 | 2 | 1
5208 | kVAh |  |  | float | 3 | 2 | 1
5210 | energy log this day 01h |  |  | float | 3 | 2 | 4
5218 | energy log this day 02h |  |  | float | 3 | 2 | 4
5226 | energy log this day 03h |  |  | float | 3 | 2 | 4
5234 | energy log this day 04h |  |  | float | 3 | 2 | 4
5242 | energy log this day 05h |  |  | float | 3 | 2 | 4
5250 | energy log this day 06h |  |  | float | 3 | 2 | 4
5258 | energy log this day 07h |  |  | float | 3 | 2 | 4
5266 | energy log this day 08h |  |  | float | 3 | 2 | 4
5274 | energy log this day 09h |  |  | float | 3 | 2 | 4
5282 | energy log this day 10h |  |  | float | 3 | 2 | 4
5290 | energy log this day 11h |  |  | float | 3 | 2 | 4
5298 | energy log this day 12h |  |  | float | 3 | 2 | 4
5306 | energy log this day 13h |  |  | float | 3 | 2 | 4
5314 | energy log this day 14h |  |  | float | 3 | 2 | 4 | 전일 디멘트 로그
5322 | energy log this day 15h |  |  | float | 3 | 2 | 4
5330 | energy log this day 16h |  |  | float | 3 | 2 | 4
5338 | energy log this day 17h |  |  | float | 3 | 2 | 4
5346 | energy log this day 18h |  |  | float | 3 | 2 | 4
5354 | energy log this day 19h |  |  | float | 3 | 2 | 4
5362 | energy log this day 20h |  |  | float | 3 | 2 | 4
5370 | energy log this day 21h |  |  | float | 3 | 2 | 4
5378 | energy log this day 22h |  |  | float | 3 | 2 | 4
5386 | energy log this day 23h |  |  | float | 3 | 2 | 4
5394 |  |  |  | U16 | 3 | 1 | 6
demand log last day
5400 | Time Stamp |  |  | U32 | 3 | 2 | 1
5402 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
5594 |  |  |  | U16 | 3 | 1 | 6
ITIC
5600 | fr |  |  | U16 | 3 | 1 | 1
5601 | re |  |  | U16 | 3 | 1 | 1
5602 | count |  |  | U16 | 3 | 1 | 1
5603 | SEQ |  |  | U16 | 3 | 1 | 1
5604 | Log #1 | start ts |  | UTC | 3 | 2 | 1
5606 |  | start ts(ms) |  | U16 | 3 | 1 | 1
5607 |  | duration |  | U16 | 3 | 1 | 1
5608 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
5609 |  | mask |  | U16 | 3 | 1 | 1
5610 |  | Level 1 |  | float | 3 | 2 | 1
5612 |  | Level 2 |  | float | 3 | 2 | 1
5614 |  | Level 3 |  | float | 3 | 2 | 1
5616 |  | Normal |  | float | 3 | 2 | 1
5618 | Log #2 |  |  | U16 | 3 | 1 | 14
5632 | Log #3 |  |  | U16 | 3 | 1 | 14
5646 | Log #4 |  |  | U16 | 3 | 1 | 14
5660 | Log #5 |  |  | U16 | 3 | 1 | 14
5674 | Log #6 |  |  | U16 | 3 | 1 | 14
5688 | Log #7 |  |  | U16 | 3 | 1 | 14
5702 | Log #8 |  |  | U16 | 3 | 1 | 14
5716 | Log #9 |  |  | U16 | 3 | 1 | 14
5730 | Log #10 |  |  | U16 | 3 | 1 | 14
5744 | Log #11 |  |  | U16 | 3 | 1 | 14
5758 | Log #12 |  |  | U16 | 3 | 1 | 14
5772 | Log #13 |  |  | U16 | 3 | 1 | 14
5786 | Log #14 |  |  | U16 | 3 | 1 | 14
5800 | Log #15 |  |  | U16 | 3 | 1 | 14
5814 | Log #16 |  |  | U16 | 3 | 1 | 14
5828 | Log #17 |  |  | U16 | 3 | 1 | 14
5842 | Log #18 |  |  | U16 | 3 | 1 | 14
5856 | Log #19 |  |  | U16 | 3 | 1 | 14
5870 | Log #20 |  |  | U16 | 3 | 1 | 14
5884 | Log #21 |  |  | U16 | 3 | 1 | 14
5898 | Log #22 |  |  | U16 | 3 | 1 | 14
5912 | Log #23 |  |  | U16 | 3 | 1 | 14
5926 | Log #24 |  |  | U16 | 3 | 1 | 14
5940 | Log #25 |  |  | U16 | 3 | 1 | 14
5954 | Log #26 |  |  | U16 | 3 | 1 | 14
5968 | Log #27 |  |  | U16 | 3 | 1 | 14
5982 | Log #28 |  |  | U16 | 3 | 1 | 14
5996 | Log #29 |  |  | U16 | 3 | 1 | 14
6010 | Log #30 |  |  | U16 | 3 | 1 | 14
6024 | Log #31 |  |  | U16 | 3 | 1 | 14
6038 | Log #32 |  |  | U16 | 3 | 1 | 14
6052 |  |  |  | U16 | 3 | 1 | 8
ITIC(Configurator)
6060 | fr |  |  | U16 | 3 | 1 | 1
6061 | re |  |  | U16 | 3 | 1 | 1
6062 | count |  |  | U16 | 3 | 1 | 1
6063 | reserved |  |  | U16 | 3 | 1 | 1
6064 | Log #1 | start ts |  | UTC | 3 | 2 | 1
6066 |  | start ts(ms) |  | U16 | 3 | 1 | 1
6067 |  | duration |  | U16 | 3 | 1 | 1
6068 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
6069 |  | mask |  | U16 | 3 | 1 | 1
6070 |  | Level 1 |  | float | 3 | 2 | 1
6072 |  | Level 2 |  | float | 3 | 2 | 1
6074 |  | Level 3 |  | float | 3 | 2 | 1
6076 |  | Normal |  | float | 3 | 2 | 1
6078 | Log #2 |  |  | U16 | 3 | 1 | 14
6092 | Log #3 |  |  | U16 | 3 | 1 | 14
6106 | Log #4 |  |  | U16 | 3 | 1 | 14
6120 | Log #5 |  |  | U16 | 3 | 1 | 14
6134 | Log #6 |  |  | U16 | 3 | 1 | 14
6148 | Log #7 |  |  | U16 | 3 | 1 | 14
6162 | Log #8 |  |  | U16 | 3 | 1 | 14
6176 | Log #9 |  |  | U16 | 3 | 1 | 14
6190 | Log #10 |  |  | U16 | 3 | 1 | 14
6204 | Log #11 |  |  | U16 | 3 | 1 | 14
6218 | Log #12 |  |  | U16 | 3 | 1 | 14
6232 | Log #13 |  |  | U16 | 3 | 1 | 14
6246 | Log #14 |  |  | U16 | 3 | 1 | 14
6260 | Log #15 |  |  | U16 | 3 | 1 | 14
6274 | Log #16 |  |  | U16 | 3 | 1 | 14
6288 | Log #17 |  |  | U16 | 3 | 1 | 14
6302 | Log #18 |  |  | U16 | 3 | 1 | 14
6316 | Log #19 |  |  | U16 | 3 | 1 | 14
6330 | Log #20 |  |  | U16 | 3 | 1 | 14
6344 | Log #21 |  |  | U16 | 3 | 1 | 14
6358 | Log #22 |  |  | U16 | 3 | 1 | 14
6372 | Log #23 |  |  | U16 | 3 | 1 | 14
6386 | Log #24 |  |  | U16 | 3 | 1 | 14
6400 | Log #25 |  |  | U16 | 3 | 1 | 14
6414 | Log #26 |  |  | U16 | 3 | 1 | 14
6428 | Log #27 |  |  | U16 | 3 | 1 | 14
6442 | Log #28 |  |  | U16 | 3 | 1 | 14
6456 | Log #29 |  |  | U16 | 3 | 1 | 14
6470 | Log #30 |  |  | U16 | 3 | 1 | 14
6484 | Log #31 |  |  | U16 | 3 | 1 | 14
6498 | Log #32 |  |  | U16 | 3 | 1 | 14
6512 |  |  |  | U16 | 3 | 1 | 8
Setting 영역 시작
PQ Event
6520 | OC Level | 정격의 2배 |  | U16 | 3,16 | 1 | 1
6521 | OC Cycle | unused |  | U16 | 3,16 | 1 | 1
6522 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
6523 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
6524 |  |  |  | U16 | 3,16 | 1 | 2
6526 | Sag Level(%), 90% | < 90% |  | U16 | 3,16 | 1 | 1
6527 | Sag Cycle | unused |  | U16 | 3,16 | 1 | 1
6528 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
6529 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
6530 |  |  |  | U16 | 3,16 | 1 | 2
6532 | Swell Level(%), 110~200~ | > 110% |  | U16 | 3,16 | 1 | 1
6533 | Swell Cycle | unused |  | U16 | 3,16 | 1 | 1
6534 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
6535 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
6536 |  |  |  | U16 | 3,16 | 1 | 2
6538 | Interruption Level, 5% | < 5% |  | U16 | 3,16 | 1 | 1
6539 | Interruption Time, 60s | unused |  | U16 | 3,16 | 1 | 1
6540 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
6541 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
6542 |  |  |  | U16 | 3,16 | 1 | 2
Transient Trigger
6544 | Transient Voltage, HoldOff Time, 20ms | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
6545 | Transient Voltage, Absolute Peak Level, 200% | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
6546 | Transient Voltage, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
6547 | Transient Voltage, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
6548 | Transient Current, HoldOff Time | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
6549 | Transient Current, Absolute Peak Level | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
6550 | Transient Current, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
6551 | Transient Current, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
6552 |  |  |  | U16 | 3,16 | 1 | 12
Recorder
Waveform
6564 | Recorder resolution(32k, 8k) |  |  | U16 | 3,16 | 1 | 1
6565 | Recorded paramater (U or I) |  |  | U16 | 3,16 | 1 | 1
6566 | pre trigger time(0.1s) |  |  | U16 | 3,16 | 1 | 1
6567 | post trigger time(1s) |  |  | U16 | 3,16 | 1 | 1
Disturbance
6568 | Recorder resolution (Half Cycle) |  |  | U16 | 3,16 | 1 | 1
6569 | Recorded parametrs(U or I) |  |  | U16 | 3,16 | 1 | 1
6570 | pre trigger time(100 sample) |  |  | U16 | 3,16 | 1 | 1
6571 | post trigger time(900 sample) |  |  | U16 | 3,16 | 1 | 1
6572 |  |  |  | U16 | 3,16 | 1 | 12
Trend Recorder
6584 | Trend Group #1 Active |  |  | U16 | 3,16 | 1 | 1
6585 | Trend Group #1 Storage Interval |  |  | U16 | 3,16 | 1 | 1
6586 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
6587 | Trend Group #1, Channel #1 |  |  | U16 | 3,16 | 1 | 1
6588 | Trend Group #1, Channel #2 |  |  | U16 | 3,16 | 1 | 1
6589 | Trend Group #1, Channel #3 |  |  | U16 | 3,16 | 1 | 1
6590 | Trend Group #1, Channel #4 |  |  | U16 | 3,16 | 1 | 1
6591 | Trend Group #1, Channel #5 |  |  | U16 | 3,16 | 1 | 1
6592 | Trend Group #1, Channel #6 |  |  | U16 | 3,16 | 1 | 1
6593 | Trend Group #1, Channel #7 |  |  | U16 | 3,16 | 1 | 1
6594 | Trend Group #1, Channel #8 |  |  | U16 | 3,16 | 1 | 1
6595 | Trend Group #1, Channel #9 |  |  | U16 | 3,16 | 1 | 1
6596 | Trend Group #1, Channel #10 |  |  | U16 | 3,16 | 1 | 1
6597 | Trend Group #1, Channel #11 |  |  | U16 | 3,16 | 1 | 1
6598 | Trend Group #1, Channel #12 |  |  | U16 | 3,16 | 1 | 1
6599 | Trend Group #1, Channel #13 |  |  | U16 | 3,16 | 1 | 1
6600 | Trend Group #1, Channel #14 |  |  | U16 | 3,16 | 1 | 1
6601 | Trend Group #1, Channel #15 |  |  | U16 | 3,16 | 1 | 1
6602 | Trend Group #1, Channel #16 |  |  | U16 | 3,16 | 1 | 1
6603 | Trend Group #2 Active |  |  | U16 | 3,16 | 1 | 1
6604 | Trend Group #2 Storage Interval |  |  | U16 | 3,16 | 1 | 1
6605 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
6606 | Trend Group #2, Channel #1 |  |  | U16 | 3,16 | 1 | 1
6607 | Trend Group #2, Channel #2 |  |  | U16 | 3,16 | 1 | 1
6608 | Trend Group #2, Channel #3 |  |  | U16 | 3,16 | 1 | 1
6609 | Trend Group #2, Channel #4 |  |  | U16 | 3,16 | 1 | 1
6610 | Trend Group #2, Channel #5 |  |  | U16 | 3,16 | 1 | 1
6611 | Trend Group #2, Channel #6 |  |  | U16 | 3,16 | 1 | 1
6612 | Trend Group #2, Channel #7 |  |  | U16 | 3,16 | 1 | 1
6613 | Trend Group #2, Channel #8 |  |  | U16 | 3,16 | 1 | 1
6614 | Trend Group #2, Channel #9 |  |  | U16 | 3,16 | 1 | 1
6615 | Trend Group #2, Channel #10 |  |  | U16 | 3,16 | 1 | 1
6616 | Trend Group #2, Channel #11 |  |  | U16 | 3,16 | 1 | 1
6617 | Trend Group #2, Channel #12 |  |  | U16 | 3,16 | 1 | 1
6618 | Trend Group #2, Channel #13 |  |  | U16 | 3,16 | 1 | 1
6619 | Trend Group #2, Channel #14 |  |  | U16 | 3,16 | 1 | 1
6620 | Trend Group #2, Channel #15 |  |  | U16 | 3,16 | 1 | 1
6621 | Trend Group #2, Channel #16 |  |  | U16 | 3,16 | 1 | 1
6622 | Trend Group #3 Active |  |  | U16 | 3,16 | 1 | 1
6623 | Trend Group #3 Storage Interval |  |  | U16 | 3,16 | 1 | 1
6624 |  |  |  | U16 | 3,16 | 1 | 1
6625 | Trend Group #3, Channel #1 |  |  | U16 | 3,16 | 1 | 1
6626 | Trend Group #3, Channel #2 |  |  | U16 | 3,16 | 1 | 1
6627 | Trend Group #3, Channel #3 |  |  | U16 | 3,16 | 1 | 1
6628 | Trend Group #3, Channel #4 |  |  | U16 | 3,16 | 1 | 1
6629 | Trend Group #3, Channel #5 |  |  | U16 | 3,16 | 1 | 1
6630 | Trend Group #3, Channel #6 |  |  | U16 | 3,16 | 1 | 1
6631 | Trend Group #3, Channel #7 |  |  | U16 | 3,16 | 1 | 1
6632 | Trend Group #3, Channel #8 |  |  | U16 | 3,16 | 1 | 1
6633 | Trend Group #3, Channel #9 |  |  | U16 | 3,16 | 1 | 1
6634 | Trend Group #3, Channel #10 |  |  | U16 | 3,16 | 1 | 1
6635 | Trend Group #3, Channel #11 |  |  | U16 | 3,16 | 1 | 1
6636 | Trend Group #3, Channel #12 |  |  | U16 | 3,16 | 1 | 1
6637 | Trend Group #3, Channel #13 |  |  | U16 | 3,16 | 1 | 1
6638 | Trend Group #3, Channel #14 |  |  | U16 | 3,16 | 1 | 1
6639 | Trend Group #3, Channel #15 |  |  | U16 | 3,16 | 1 | 1
6640 | Trend Group #3, Channel #16 |  |  | U16 | 3,16 | 1 | 1
6641 | Trend Group #4 Active |  |  | U16 | 3,16 | 1 | 1
6642 | Trend Group #4 Storage Interval |  |  | U16 | 3,16 | 1 | 1
6643 |  |  |  | U16 | 3,16 | 1 | 1
6644 | Trend Group #4, Channel #1 |  |  | U16 | 3,16 | 1 | 1
6645 | Trend Group #4, Channel #2 |  |  | U16 | 3,16 | 1 | 1
6646 | Trend Group #4, Channel #3 |  |  | U16 | 3,16 | 1 | 1
6647 | Trend Group #4, Channel #4 |  |  | U16 | 3,16 | 1 | 1
6648 | Trend Group #4, Channel #5 |  |  | U16 | 3,16 | 1 | 1
6649 | Trend Group #4, Channel #6 |  |  | U16 | 3,16 | 1 | 1
6650 | Trend Group #4, Channel #7 |  |  | U16 | 3,16 | 1 | 1
6651 | Trend Group #4, Channel #8 |  |  | U16 | 3,16 | 1 | 1
6652 | Trend Group #4, Channel #9 |  |  | U16 | 3,16 | 1 | 1
6653 | Trend Group #4, Channel #10 |  |  | U16 | 3,16 | 1 | 1
6654 | Trend Group #4, Channel #11 |  |  | U16 | 3,16 | 1 | 1
6655 | Trend Group #4, Channel #12 |  |  | U16 | 3,16 | 1 | 1
6656 | Trend Group #4, Channel #13 |  |  | U16 | 3,16 | 1 | 1
6657 | Trend Group #4, Channel #14 |  |  | U16 | 3,16 | 1 | 1
6658 | Trend Group #4, Channel #15 |  |  | U16 | 3,16 | 1 | 1
6659 | Trend Group #4, Channel #16 |  |  | U16 | 3,16 | 1 | 1
6660 |  |  |  | U16 | 3,16 | 1 | 4
Power Quality Report
6664 | Active |  |  | U16 | 3,16 | 1 | 1
6665 | Start Day |  |  | U16 | 3,16 | 1 | 1
6666 |  |  |  | U16 |  | 1 | 8
Alarm Definition
6674 | compare Time Delay(1s) |  |  | U16 | 3,16 | 1 | 1
6675 |  |  |  | U16 |  | 1 | 1
6676 |  |  |  | U16 |  | 1 | 1
6677 |  |  |  | U16 |  | 1 | 1
Alarm Settings
6678 | Alarm Info #1 Channel(0:disabled, >0: enabled) |  |  | U16 | 3,16 | 1 | 1
6679 | Alarm Cond (0: < , 1:>) |  |  | U16 | 3,16 | 1 | 1
6680 | Hysteresis (% of Nominal) |  |  | U16 | 3,16 | 1 | 1
6681 | Alarm Action (None, Relay or Beep) |  |  | U16 | 3,16 | 1 | 1
6682 | Alarm Level |  |  | float | 3,16 | 2 | 1
6684 | Alarm Settings #2 |  |  | U16 | 3,16 | 1 | 6
6690 | Alarm Settings #3 |  |  | U16 | 3,16 | 1 | 6
6696 | Alarm Settings #4 |  |  | U16 | 3,16 | 1 | 6
6702 | Alarm Settings #5 |  |  | U16 | 3,16 | 1 | 6
6708 | Alarm Settings #6 |  |  | U16 | 3,16 | 1 | 6
6714 | Alarm Settings #7 |  |  | U16 | 3,16 | 1 | 6
6720 | Alarm Settings #8 |  |  | U16 | 3,16 | 1 | 6
6726 | Alarm Settings #9 |  |  | U16 | 3,16 | 1 | 6
6732 | Alarm Settings #10 |  |  | U16 | 3,16 | 1 | 6
6738 | Alarm Settings #11 |  |  | U16 | 3,16 | 1 | 6
6744 | Alarm Settings #12 |  |  | U16 | 3,16 | 1 | 6
6750 | Alarm Settings #13 |  |  | U16 | 3,16 | 1 | 6
6756 | Alarm Settings #14 |  |  | U16 | 3,16 | 1 | 6
6762 | Alarm Settings #15 |  |  | U16 | 3,16 | 1 | 6
6768 | Alarm Settings #16 |  |  | U16 | 3,16 | 1 | 6
6774 | Alarm Settings #17 |  |  | U16 | 3,16 | 1 | 6
6780 | Alarm Settings #18 |  |  | U16 | 3,16 | 1 | 6
6786 | Alarm Settings #19 |  |  | U16 | 3,16 | 1 | 6
6792 | Alarm Settings #20 |  |  | U16 | 3,16 | 1 | 6
6798 | Alarm Settings #21 |  |  | U16 | 3,16 | 1 | 6
6804 | Alarm Settings #22 |  |  | U16 | 3,16 | 1 | 6
6810 | Alarm Settings #23 |  |  | U16 | 3,16 | 1 | 6
6816 | Alarm Settings #24 |  |  | U16 | 3,16 | 1 | 6
6822 | Alarm Settings #25 |  |  | U16 | 3,16 | 1 | 6
6828 | Alarm Settings #26 |  |  | U16 | 3,16 | 1 | 6
6834 | Alarm Settings #27 |  |  | U16 | 3,16 | 1 | 6
6840 | Alarm Settings #28 |  |  | U16 | 3,16 | 1 | 6
6846 | Alarm Settings #29 |  |  | U16 | 3,16 | 1 | 6
6852 | Alarm Settings #30 |  |  | U16 | 3,16 | 1 | 6
6858 | Alarm Settings #31 |  |  | U16 | 3,16 | 1 | 6
6864 | Alarm Settings #32 |  |  | U16 | 3,16 | 1 | 6
6870

## #2CH modbus
address | name | 설명 | Unit | TYPE | FC | Word Count | Item Count
Metering
10000 | Time Stamp |  |  | UTC | 3 | 2 | 1
10002 | TYPE |  |  | U16 | 3 | 1 | 1
10003 | STATUS | 1 : online, 0 : offline |  | U16 | 3 | 1 | 1
10004 | Frequency | 라인주파수 | Hz | float | 3 | 2 | 1
10006 | Internal Temp |  | ℃ | float | 3 | 2 | 1
10008 | U1 | 상전압 1 | V | float | 3 | 2 | 1
10010 | U2 | 상전압 2 |  | float | 3 | 2 | 1
10012 | U3 | 상전압 3 |  | float | 3 | 2 | 1
10014 | U~ | 상전압 평균 |  | float | 3 | 2 | 1
10016 | U12 | 선간 전압 12 |  | float | 3 | 2 | 1
10018 | U23 | 선간 전압 23 |  | float | 3 | 2 | 1
10020 | U31 | 선간 전압 31 |  | float | 3 | 2 | 1
10022 | Upp~ | 선간 전압 평균 |  | float | 3 | 2 | 1
10024 | Uunbalance2 |  | % | float | 3 | 2 | 1
10026 | Uunbalance0 |  |  | float | 3 | 2 | 1
10028 | U Zero Sequence Mag. |  |  | float | 3 | 2 | 1
10030 | U Zero Sequence angle |  |  | float | 3 | 2 | 1
10032 | U Positive Sequence Mag. |  |  | float | 3 | 2 | 1
10034 | U Positive Sequence angle |  |  | float | 3 | 2 | 1
10036 | U Negative Sequence Mag |  |  | float | 3 | 2 | 1
10038 | U Negative Sequence angle |  |  | float | 3 | 2 | 1
10040 | Angle U1 |  |  | float | 3 | 2 | 1
10042 | Angle U2 |  |  | float | 3 | 2 | 1
10044 | Angle U3 |  |  | float | 3 | 2 | 1
10046 | U Underdeviation L1 |  | % | float | 3 | 2 | 1
10048 | U Underdeviation L2 |  | % | float | 3 | 2 | 1
10050 | U Underdeviation L3 |  | % | float | 3 | 2 | 1
10052 | U Overdeviation L1 |  | % | float | 3 | 2 | 1
10054 | U Overdeviation L2 |  | % | float | 3 | 2 | 1
10056 | U Overdeviation L3 |  | % | float | 3 | 2 | 1
10058 | I1 | 상전류 1 | A | float | 3 | 2 | 1
10060 | I2 | 상전류 2 |  | float | 3 | 2 | 1
10062 | I3 | 상전류 3 |  | float | 3 | 2 | 1
10064 | I~ |  |  | float | 3 | 2 | 1
10066 | I total (I1+I2+I3) |  |  | float | 3 | 2 | 1
10068 | In(Measured) |  |  | float | 3 | 2 | 1
10070 | In(Calculated) | Ia+Ib+Ic+In = Ig |  | float | 3 | 2 | 1
10072 | Ig |  |  | float | 3 | 2 | 1
10074 | I Zero Sequence Mag |  |  | float | 3 | 2 | 1
10076 | I Zero Sequence angle |  |  | float | 3 | 2 | 1
10078 | I Positive Sequence Mag. |  |  | float | 3 | 2 | 1
10080 | I Positive Sequence angle |  |  | float | 3 | 2 | 1
10082 | I Negative Sequence Mag. |  |  | float | 3 | 2 | 1
10084 | I Negative Sequence angle |  |  | float | 3 | 2 | 1
10086 | Angle I1 |  |  | float | 3 | 2 | 1
10088 | Angle I2 |  |  | float | 3 | 2 | 1
10090 | Angle I3 |  |  | float | 3 | 2 | 1
10092 | Iunbalance2 |  | % | float | 3 | 2 | 1
10094 | Iunbalance0 |  |  | float | 3 | 2 | 1
10096 | P1 | 유효전력 P1 | W | float | 3 | 2 | 1
10098 | P2 | 유효전력 P2 |  | float | 3 | 2 | 1
10100 | P3 | 유효전력 P3 |  | float | 3 | 2 | 1
10102 | P total | 유효전력 P-total |  | float | 3 | 2 | 1
10104 | fP1 |  |  | float | 3 | 2 | 1
10106 | fP2 |  |  | float | 3 | 2 | 1
10108 | fP3 |  |  | float | 3 | 2 | 1
10110 | fP total |  |  | float | 3 | 2 | 1
10112 | Q1 | 무효전력 Q1 | VAR | float | 3 | 2 | 1
10114 | Q2 | 무효전력 Q2 |  | float | 3 | 2 | 1
10116 | Q3 | 무효전력 Q3 |  | float | 3 | 2 | 1
10118 | Q total | 무효전력 Q-total |  | float | 3 | 2 | 1
10120 | fQ1 |  |  | float | 3 | 2 | 1
10122 | fQ2 |  |  | float | 3 | 2 | 1
10124 | fQ3 |  |  | float | 3 | 2 | 1
10126 | fQ total |  |  | float | 3 | 2 | 1
10128 | S1 | 피상전력 S1 | VA | float | 3 | 2 | 1
10130 | S2 | 피상전력 S2 |  | float | 3 | 2 | 1
10132 | S3 | 피상전력 S3 |  | float | 3 | 2 | 1
10134 | S total | 피상전력 S-total |  | float | 3 | 2 | 1
10136 | fS1 |  |  | float | 3 | 2 | 1
10138 | fS2 |  |  | float | 3 | 2 | 1
10140 | fS3 |  |  | float | 3 | 2 | 1
10142 | fS total |  |  | float | 3 | 2 | 1
10144 | PF1 | 역률 PF1 | % | float | 3 | 2 | 1
10146 | PF2 | 역률 PF2 |  | float | 3 | 2 | 1
10148 | PF3 | 역률 PF3 |  | float | 3 | 2 | 1
10150 | PF total | 역률 PF-total |  | float | 3 | 2 | 1
10152 | dPF1 |  | % | float | 3 | 2 | 1
10154 | dPF2 |  |  | float | 3 | 2 | 1
10156 | dPF3 |  |  | float | 3 | 2 | 1
10158 | dPF total |  |  | float | 3 | 2 | 1
10160 | deformed Power D L1 |  | W | float | 3 | 2 | 1
10162 | deformed Power D L2 |  |  | float | 3 | 2 | 1
10164 | deformed Power D L3 |  |  | float | 3 | 2 | 1
10166 | deformed Power D Total |  |  | float | 3 | 2 | 1
10168 | Power Angle(atan(fPt,fQt) L1 |  | Degree | float | 3 | 2 | 1
10170 | Power Angle(atan(fPt,fQt) L2 |  |  | float | 3 | 2 | 1
10172 | Power Angle(atan(fPt,fQt) L3 |  |  | float | 3 | 2 | 1
10174 |  |  |  | float | 3 | 2 | 1
10176 | THD V1 |  | % | float | 3 | 2 | 1
10178 | THD V2 |  |  | float | 3 | 2 | 1
10180 | THD V3 |  |  | float | 3 | 2 | 1
10182 | THD V12 |  |  | float | 3 | 2 | 1
10184 | THD V23 |  |  | float | 3 | 2 | 1
10186 | THD V31 |  |  | float | 3 | 2 | 1
10188 | CF V1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
10190 | CF V2 |  |  | float | 3 | 2 | 1
10192 | CF V3 |  |  | float | 3 | 2 | 1
10194 | CF V12 |  |  | float | 3 | 2 | 1
10196 | CF V23 |  |  | float | 3 | 2 | 1
10198 | CF V31 |  |  | float | 3 | 2 | 1
10200 | THD I1 |  |  | float | 3 | 2 | 1
10202 | THD I2 |  |  | float | 3 | 2 | 1
10204 | THD I3 |  |  | float | 3 | 2 | 1
10206 | TDD I1 |  |  | float | 3 | 2 | 1
10208 | TDD I2 |  |  | float | 3 | 2 | 1
10210 | TDD I3 |  |  | float | 3 | 2 | 1
10212 | K I1 | K-FACTOR : 고조파 허용율 |  | float | 3 | 2 | 1
10214 | K I2 |  |  | float | 3 | 2 | 1
10216 | K I3 |  |  | float | 3 | 2 | 1
10218 | CF I1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
10220 | CF I2 |  |  | float | 3 | 2 | 1
10222 | CF I3 |  |  | float | 3 | 2 | 1
10224 | fU1 | 기본파 U1 | V | float | 3 | 2 | 1
10226 | fU2 | 기본파 U2 |  | float | 3 | 2 | 1
10228 | fU3 | 기본파 U3 |  | float | 3 | 2 | 1
10230 | fU~ | 기본파 전압 평균 |  | float | 3 | 2 | 1
10232 | fI1 | 기본파 I1 | A | float | 3 | 2 | 1
10234 | fI2 | 기본파 I2 |  | float | 3 | 2 | 1
10236 | fI3 | 기본파 I3 |  | float | 3 | 2 | 1
10238 | fI~ | 기본파 전류 평균 |  | float | 3 | 2 | 1
Energy
10240 | import kwh(0 ~ 999,999,999.9 kw) | 누적 유효전력량 |  | U32 | 3 | 2 | 1
10242 | export kwh |  |  | U32 | 3 | 2 | 1
10244 | import kvarh |  |  | U32 | 3 | 2 | 1
10246 | export kvarh |  |  | U32 | 3 | 2 | 1
10248 | kvah |  |  | U32 | 3 | 2 | 1
10250 |  |  |  | U32 | 3 | 2 | 1
10252 | import kwh this month |  |  | U32 | 3 | 2 | 1
10254 | export kwh this month |  |  | U32 | 3 | 2 | 1
10256 | import kvarh this month |  |  | U32 | 3 | 2 | 1
10258 | export kvarh this month |  |  | U32 | 3 | 2 | 1
10260 | kvah this month |  |  | U32 | 3 | 2 | 1
10262 |  |  |  | U32 | 3 | 2 | 1
10264 | import kwh last month |  |  | U32 | 3 | 2 | 1
10266 | export kwh last month |  |  | U32 | 3 | 2 | 1
10268 | import kvarh last month |  |  | U32 | 3 | 2 | 1
10270 | export kvarh last month |  |  | U32 | 3 | 2 | 1
10272 | kvah last month |  |  | U32 | 3 | 2 | 1
10274 |  |  |  | U32 | 3 | 2 | 1
10276 | import kwh | 0~999,999,999.999 kw |  | U64 | 3 | 4 | 1
10280 | export kwh |  |  | U64 | 3 | 4 | 1
10284 | import kvarh |  |  | U64 | 3 | 4 | 1
10288 | export kvarh |  |  | U64 | 3 | 4 | 1
10292 | kvah |  |  | U64 | 3 | 4 | 1
10296 |  |  |  | U64 | 3 | 4 | 1
Demand
10300 | Time Stamp |  |  | UTC | 3 | 2 | 1
10302 | Max Demand P(import) |  |  | float | 3 | 2 | 1
10304 | Time Stamp |  |  | UTC | 3 | 2 | 1
10306 | Max Demand P(export) |  |  | float | 3 | 2 | 1
10308 | Time Stamp |  |  | UTC | 3 | 2 | 1
10310 | Max Demand Q(import) |  |  | float | 3 | 2 | 1
10312 | Time Stamp |  |  | UTC | 3 | 2 | 1
10314 | Max Demand Q(export) |  |  | float | 3 | 2 | 1
10316 | Time Stamp |  |  | UTC | 3 | 2 | 1
10318 | Max Demand S |  |  | float | 3 | 2 | 1
10320 | Time Stamp |  |  | UTC | 3 | 2 | 1
10322 | Max Demand I1 |  |  | float | 3 | 2 | 1
10324 | Time Stamp |  |  | UTC | 3 | 2 | 1
10326 | Max Demand I2 |  |  | float | 3 | 2 | 1
10328 | Time Stamp |  |  | UTC | 3 | 2 | 1
10330 | Max Demand I3 |  |  | float | 3 | 2 | 1
10332 | Demand time stamp |  |  | UTC | 3 | 2 | 1
10334 | Demand P(import) |  |  | float | 3 | 2 | 1
10336 | Demand P(export) |  |  | float | 3 | 2 | 1
10338 | Demand Q(import) |  |  | float | 3 | 2 | 1
10340 | Demand Q(export) |  |  | float | 3 | 2 | 1
10342 | Demand S(export) |  |  | float | 3 | 2 | 1
10344 | Demand I1 |  |  | float | 3 | 2 | 1
10346 | Demand I2 |  |  | float | 3 | 2 | 1
10348 | Demand I3 |  |  | float | 3 | 2 | 1
10350 | Present Demand P(import) |  |  | float | 3 | 2 | 1
10352 | Present Demand P(export) |  |  | float | 3 | 2 | 1
10354 | Present Demand Q(import) |  |  | float | 3 | 2 | 1
10356 | Present Demand Q(export) |  |  | float | 3 | 2 | 1
10358 | Present Demand S(export) |  |  | float | 3 | 2 | 1
10360 | Forecast Demand P(export) |  |  | float | 3 | 2 | 1
10362 | Demand P 15m(import) |  |  | float | 3 | 2 | 1
10364 |  |  |  | float | 3 | 2 | 1
10366 |  |  |  | float | 3 | 2 | 1
10368 | Time Stamp(Demand Log 시작일) |  |  | U32 | 3 | 2 | 1
10370 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
10562 |  |  |  | float | 3 | 2 | 19
Voltage Quality RealTime Value
10600 | Voltage Under Deviation L1 |  | % | float | 3 | 2 | 1
10602 | Voltage Under Deviation L2 |  | % | float | 3 | 2 | 1
10604 | Voltage Under Deviation L3 |  | % | float | 3 | 2 | 1
10606 | Voltage Under Value L1 |  | rms | float | 3 | 2 | 1
10608 | Voltage Under Value L2 |  | rms | float | 3 | 2 | 1
10610 | Voltage Under Value L3 |  | rms | float | 3 | 2 | 1
10612 | Voltage Over Deviation L1 |  | % | float | 3 | 2 | 1
10614 | Voltage Over Deviation L2 |  | % | float | 3 | 2 | 1
10616 | Voltage Over Deviation L3 |  | % | float | 3 | 2 | 1
10618 | Voltage Over Value L1 |  | rms | float | 3 | 2 | 1
10620 | Voltage Over Value L2 |  | rms | float | 3 | 2 | 1
10622 | Voltage Over Value L3 |  | rms | float | 3 | 2 | 1
10624 | Flickers Pi L1 | 150/180 Cycles |  | float | 3 | 2 | 1
10626 | Flickers Pi L2 |  |  | float | 3 | 2 | 1
10628 | Flickers Pi L3 |  |  | float | 3 | 2 | 1
10630 | Flicker Pst L1 | 10min |  | float | 3 | 2 | 1
10632 | Flicker Pst L2 |  |  | float | 3 | 2 | 1
10634 | Flicker Pst L3 |  |  | float | 3 | 2 | 1
10636 | Flicker Plt L1 | 2hr |  | float | 3 | 2 | 1
10638 | Flicker Plt L2 |  |  | float | 3 | 2 | 1
10640 | Flicker Plt L3 |  |  | float | 3 | 2 | 1
10642 | Signaling Volt L1 | Magnitude of current 10/12 cycles as a percentage of nominal voltage. |  | float | 3 | 2 | 1
10644 | Signaling Volt L2 |  |  | float | 3 | 2 | 1
10646 | Signaling Volt L3 |  |  | float | 3 | 2 | 1
10648 | Signaling Volt Max L1 | Maximum magnitude of MSV from recording started as a percentage of nominal voltage |  | float | 3 | 2 | 1
10650 | Signaling Volt Max L2 |  |  | float | 3 | 2 | 1
10652 | Signaling Volt Max L3 |  |  | float | 3 | 2 | 1
10654 |  |  |  | float | 3 | 2 | 23
EN50160 This Week
10700 | start date |  |  | UTC | 3 | 2 | 1
10702 | end date |  |  | UTC | 3 | 2 | 1
10704 | status&compliance | bit 0: Freq Var1 bit 1: Freq Var2 bit 2: Volt Var1 L1 bit 3: Volt Var1 L2 bit 4: Volt Var1 L3 bit 5: Volt Var2 L1 bit 6: Volt Var2 L2 bit 7: Volt Var2 L3 bit 8: Unbalance bit 9: Volt THD L1 bit 10: Volt THD L2 bit 11: Volt THD L3 bit 12: Volt HD L1 bit 13: Volt HD L2 bit 14: Volt HD L3 bit 15: Pst L1 bit 16: Pst L2 bit 17: Pst L3 bit 18: Plt L1 bit 19: Plt L2 bit 20: Plt L3 bit 21: SigVolt L1 bit 22: SigVolt L2 bit 23: SigVolt L3 bit 31: Complete [status] 0: OK 1: failed |  | U32 | 3 | 2 | 1
10706 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1
10707 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1
10708 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
10709 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
10710 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1
10711 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
10712 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
10713 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1
10714 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
10715 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
10716 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1
10717 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
10718 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
10719 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1
10720 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
10721 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
10722 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1
10723 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
10724 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
10725 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1
10726 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
10727 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
10728 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1
10729 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
10730 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
10731 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1
10732 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
10733 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
10734 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
10735 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
10736 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
10737 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
10738 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
10739 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
10740 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
10741 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
10742 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
10743 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
10744 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
10745 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
10746 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
10747 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
10748 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
10749 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
EN50160 Last Week
10750 | start date |  |  | UTC | 3 | 2 | 1
10752 | end date |  |  | UTC | 3 | 2 | 1
10754 | status |  |  | U16 | 3 | 1 | 1
10755 | compilance |  |  | U16 | 3 | 1 | 1
10756 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1
10757 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1
10758 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
10759 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
10760 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1
10761 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
10762 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
10763 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1
10764 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
10765 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
10766 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1
10767 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
10768 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
10769 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1
10770 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
10771 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
10772 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1
10773 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
10774 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
10775 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1
10776 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
10777 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
10778 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1
10779 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
10780 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
10781 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1
10782 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
10783 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
10784 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
10785 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
10786 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
10787 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
10788 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
10789 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
10790 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
10791 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
10792 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
10793 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
10794 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
10795 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
10796 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
10797 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
10798 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
10799 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
Harmonics
10800 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
10864 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
10928 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
10992 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
11056 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
11120 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
11184 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
11248 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
11312 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
11376 |  |  |  | S16 | 3 | 1 | 24
Inter Harmonics
11400 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
11464 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
11528 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
11592 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
11656 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
11720 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
11784 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
11848 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
11912 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
11976 |  |  |  | S16 | 3 | 1 | 24
Max/Min
12000 | fr |  |  | U16 | 3 | 1 | 1
12001 | re |  |  | U16 | 3 | 1 | 1
12002 | Reset TimeStamp |  |  | UTC | 3 | 2 | 1
12004 | Frequency | Max |  | float | 3 | 2 | 1
12006 |  | Max Timestamp |  | UTC | 3 | 2 | 1
12008 |  | Min |  | float | 3 | 2 | 1
12010 |  | Min Timestamp |  | UTC | 3 | 2 | 1
12012 | Temp |  |  | float | 3 | 2 | 4
12020 | U1 |  |  | float | 3 | 2 | 4
12028 | U2 |  |  | float | 3 | 2 | 4
12036 | U3 |  |  | float | 3 | 2 | 4
12044 | U~ |  |  | float | 3 | 2 | 4
12052 | U12 |  |  | float | 3 | 2 | 4
12060 | U23 |  |  | float | 3 | 2 | 4
12068 | U31 |  |  | float | 3 | 2 | 4
12076 | Upp~ |  |  | float | 3 | 2 | 4
12084 | I1 |  |  | float | 3 | 2 | 4
12092 | I2 |  |  | float | 3 | 2 | 4
12100 | I3 |  |  | float | 3 | 2 | 4
12108 | I~ |  |  | float | 3 | 2 | 4
12116 | I total |  |  | float | 3 | 2 | 4
12124 | In |  |  | float | 3 | 2 | 4
12132 | Isum |  |  | float | 3 | 2 | 4
12140 | P1 |  |  | float | 3 | 2 | 4
12148 | P2 |  |  | float | 3 | 2 | 4
12156 | P3 |  |  | float | 3 | 2 | 4
12164 | P total |  |  | float | 3 | 2 | 4
12172 | Q1 |  |  | float | 3 | 2 | 4
12180 | Q2 |  |  | float | 3 | 2 | 4
12188 | Q3 |  |  | float | 3 | 2 | 4
12196 | Q total |  |  | float | 3 | 2 | 4
12204 | S1 |  |  | float | 3 | 2 | 4
12212 | S2 |  |  | float | 3 | 2 | 4
12220 | S3 |  |  | float | 3 | 2 | 4
12228 | S total |  |  | float | 3 | 2 | 4
12236 | PF L1 |  |  | float | 3 | 2 | 4
12244 | PF L2 |  |  | float | 3 | 2 | 4
12252 | PF L3 |  |  | float | 3 | 2 | 4
12260 | PF total |  |  | float | 3 | 2 | 4
12268 | THD U1 |  |  | float | 3 | 2 | 4
12276 | THD U2 |  |  | float | 3 | 2 | 4
12284 | THD U3 |  |  | float | 3 | 2 | 4
12292 | THD U12 |  |  | float | 3 | 2 | 4
12300 | THD U23 |  |  | float | 3 | 2 | 4
12308 | THD U31 |  |  | float | 3 | 2 | 4
12316 | THD I1 |  |  | float | 3 | 2 | 4
12324 | THD I2 |  |  | float | 3 | 2 | 4
12332 | THD I3 |  |  | float | 3 | 2 | 4
12340 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
12342 | reserved |  |  | U16 | 3 | 1 | 1
12343 | CRC |  |  | U16 | 3 | 1 | 1
12344 |  |  |  | U16 | 3 | 1 | 6
alarm status
12350 | fr |  |  | U16 | 3 | 1 | 1
12351 | re |  |  | U16 | 3 | 1 | 1
12352 | reset Ts |  |  | UTC | 3 | 2 | 1
12354 | Alarm State #1 | Alarm Channel |  | U16 | 3 | 1 | 1
12355 |  | Alarm Condition |  | U16 | 3 | 1 | 1
12356 |  | Alarm Level |  | float | 3 | 2 | 1
12358 |  | Alarm Status |  | U16 | 3 | 1 | 1
12359 |  | Alarm Count |  | U16 | 3 | 1 | 1
12360 | Alarm State #2 |  |  | U16 | 3 | 1 | 6
12366 | Alarm State #3 |  |  | U16 | 3 | 1 | 6
12372 | Alarm State #4 |  |  | U16 | 3 | 1 | 6
12378 | Alarm State #5 |  |  | U16 | 3 | 1 | 6
12384 | Alarm State #6 |  |  | U16 | 3 | 1 | 6
12390 | Alarm State #7 |  |  | U16 | 3 | 1 | 6
12396 | Alarm State #8 |  |  | U16 | 3 | 1 | 6
12402 | Alarm State #9 |  |  | U16 | 3 | 1 | 6
12408 | Alarm State #10 |  |  | U16 | 3 | 1 | 6
12414 | Alarm State #11 |  |  | U16 | 3 | 1 | 6
12420 | Alarm State #12 |  |  | U16 | 3 | 1 | 6
12426 | Alarm State #13 |  |  | U16 | 3 | 1 | 6
12432 | Alarm State #14 |  |  | U16 | 3 | 1 | 6
12438 | Alarm State #15 |  |  | U16 | 3 | 1 | 6
12444 | Alarm State #16 |  |  | U16 | 3 | 1 | 6
12450 | Alarm State #17 |  |  | U16 | 3 | 1 | 6
12456 | Alarm State #18 |  |  | U16 | 3 | 1 | 6
12462 | Alarm State #19 |  |  | U16 | 3 | 1 | 6
12468 | Alarm State #20 |  |  | U16 | 3 | 1 | 6
12474 | Alarm State #21 |  |  | U16 | 3 | 1 | 6
12480 | Alarm State #22 |  |  | U16 | 3 | 1 | 6
12486 | Alarm State #23 |  |  | U16 | 3 | 1 | 6
12492 | Alarm State #24 |  |  | U16 | 3 | 1 | 6
12498 | Alarm State #25 |  |  | U16 | 3 | 1 | 6
12504 | Alarm State #26 |  |  | U16 | 3 | 1 | 6
12510 | Alarm State #27 |  |  | U16 | 3 | 1 | 6
12516 | Alarm State #28 |  |  | U16 | 3 | 1 | 6
12522 | Alarm State #29 |  |  | U16 | 3 | 1 | 6
12528 | Alarm State #30 |  |  | U16 | 3 | 1 | 6
12534 | Alarm State #31 |  |  | U16 | 3 | 1 | 6
12540 | Alarm State #32 |  |  | U16 | 3 | 1 | 6
12546 | update Ts |  |  | U32 | 3 | 2 | 1
12548 | Global Alarm Status | (alarm 하나라도 있으면 1, 아니면 0) |  | U16 | 3 | 1 | 1
12549 |  |  |  | U16 | 3 | 1 | 1
alarm log
12550 | fr | 0 ~ 1023 |  | U16 | 3 | 1 | 1
12551 | re | 0 ~ 1023 |  | U16 | 3 | 1 | 1
12552 | count | 전체 log 수 |  | U16 | 3 | 1 | 1
12553 | seq |  |  | U16 | 3 | 1 | 1
12554 | Alarm Log #1 | Time Stamp |  | UTC | 3 | 2 | 1
12556 |  | status |  | U16 | 3 | 1 | 1
12557 |  | Alarm Channel & Condition |  | U16 | 3 | 1 | 1
12558 |  | level |  | float | 3 | 2 | 1
12560 |  | Value |  | float | 3 | 2 | 1
12562 | Alarm Log #2 |  |  | U16 | 3 | 1 | 8
12570 | Alarm Log #3 |  |  | U16 | 3 | 1 | 8
12578 | Alarm Log #4 |  |  | U16 | 3 | 1 | 8
12586 | Alarm Log #5 |  |  | U16 | 3 | 1 | 8
12594 | Alarm Log #6 |  |  | U16 | 3 | 1 | 8
12602 | Alarm Log #7 |  |  | U16 | 3 | 1 | 8
12610 | Alarm Log #8 |  |  | U16 | 3 | 1 | 8
12618 | Alarm Log #9 |  |  | U16 | 3 | 1 | 8
12626 | Alarm Log #10 |  |  | U16 | 3 | 1 | 8
12634 | Alarm Log #11 |  |  | U16 | 3 | 1 | 8
12642 | Alarm Log #12 |  |  | U16 | 3 | 1 | 8
12650 | Alarm Log #13 |  |  | U16 | 3 | 1 | 8
12658 | Alarm Log #14 |  |  | U16 | 3 | 1 | 8
12666 | Alarm Log #15 |  |  | U16 | 3 | 1 | 8
12674 | Alarm Log #16 |  |  | U16 | 3 | 1 | 8
12682 | Alarm Log #17 |  |  | U16 | 3 | 1 | 8
12690 | Alarm Log #18 |  |  | U16 | 3 | 1 | 8
12698 | Alarm Log #19 |  |  | U16 | 3 | 1 | 8
12706 | Alarm Log #20 |  |  | U16 | 3 | 1 | 8
12714 | Alarm Log #21 |  |  | U16 | 3 | 1 | 8
12722 | Alarm Log #22 |  |  | U16 | 3 | 1 | 8
12730 | Alarm Log #23 |  |  | U16 | 3 | 1 | 8
12738 | Alarm Log #24 |  |  | U16 | 3 | 1 | 8
12746 | Alarm Log #25 |  |  | U16 | 3 | 1 | 8
12754 | Alarm Log #26 |  |  | U16 | 3 | 1 | 8
12762 | Alarm Log #27 |  |  | U16 | 3 | 1 | 8
12770 | Alarm Log #28 |  |  | U16 | 3 | 1 | 8
12778 | Alarm Log #29 |  |  | U16 | 3 | 1 | 8
12786 | Alarm Log #30 |  |  | U16 | 3 | 1 | 8
12794 | Alarm Log #31 |  |  | U16 | 3 | 1 | 8
12802 | Alarm Log #32 |  |  | U16 | 3 | 1 | 8
12810 |  |  |  | U16 | 3 | 1 | 40
이벤트 리스트
12850 | fr | 0 ~ 1023 |  | U16 | 3 | 1 | 1
12851 | re | 0 ~ 1023 |  | U16 | 3 | 1 | 1
12852 | count | 0 ~ 1023 |  | U16 | 3 | 1 | 1
12853 | seq |  |  | U16 | 3 | 1 | 1
PQ 이벤트(Sag, Swell, Transient, OC)
12854 | start ts |  |  | UTC | 3 | 2 | 1
12856 | start ts(ms) |  |  | U16 | 3 | 1 | 1
12857 | duration |  |  | U16 | 3 | 1 | 1
12858 | type | 1 : E_SAG 2 : E_SWELL 3 : E_sINTR 4 : E_lINTR 5 : E_OC 6 : E_RVC 7 : E_TrV 8 : E_TrC |  | U16 | 3 | 1 | 1
12859 | mask |  |  | U16 | 3 | 1 | 1
12860 | Level 1 |  |  | float | 3 | 2 | 1
12862 | Level 2 |  |  | float | 3 | 2 | 1
12864 | Level 3 |  |  | float | 3 | 2 | 1
12866 | PQ Event #2 |  |  | U16 | 3 | 1 | 12
12878 | PQ Event #3 |  |  | U16 | 3 | 1 | 12
12890 | PQ Event #4 |  |  | U16 | 3 | 1 | 12
12902 | PQ Event #5 |  |  | U16 | 3 | 1 | 12
12914 | PQ Event #6 |  |  | U16 | 3 | 1 | 12
12926 | PQ Event #7 |  |  | U16 | 3 | 1 | 12
12938 | PQ Event #8 |  |  | U16 | 3 | 1 | 12
12950 | PQ Event #9 |  |  | U16 | 3 | 1 | 12
12962 | PQ Event #10 |  |  | U16 | 3 | 1 | 12
12974 | PQ Event #11 |  |  | U16 | 3 | 1 | 12
12986 | PQ Event #12 |  |  | U16 | 3 | 1 | 12
12998 | PQ Event #13 |  |  | U16 | 3 | 1 | 12
13010 | PQ Event #14 |  |  | U16 | 3 | 1 | 12
13022 | PQ Event #15 |  |  | U16 | 3 | 1 | 12
13034 | PQ Event #16 |  |  | U16 | 3 | 1 | 12
13046 | PQ Event #17 |  |  | U16 | 3 | 1 | 12
13058 | PQ Event #18 |  |  | U16 | 3 | 1 | 12
13070 | PQ Event #19 |  |  | U16 | 3 | 1 | 12
13082 | PQ Event #20 |  |  | U16 | 3 | 1 | 12
13094 | PQ Event #21 |  |  | U16 | 3 | 1 | 12
13106 | PQ Event #22 |  |  | U16 | 3 | 1 | 12
13118 | PQ Event #23 |  |  | U16 | 3 | 1 | 12
13130 | PQ Event #24 |  |  | U16 | 3 | 1 | 12
13142 | PQ Event #25 |  |  | U16 | 3 | 1 | 12
13154 | PQ Event #26 |  |  | U16 | 3 | 1 | 12
13166 | PQ Event #27 |  |  | U16 | 3 | 1 | 12
13178 | PQ Event #28 |  |  | U16 | 3 | 1 | 12
13190 | PQ Event #29 |  |  | U16 | 3 | 1 | 12
13202 | PQ Event #30 |  |  | U16 | 3 | 1 | 12
13214 | PQ Event #31 |  |  | U16 | 3 | 1 | 12
13226 | PQ Event #32 |  |  | U16 | 3 | 1 | 12
13238 |  |  |  | U16 | 3 | 1 | 2
PQ Event Counter
13240 |  |  |  | U16 | 3 | 1 | 1
13241 |  |  |  | U16 | 3 | 1 | 1
13242 |  |  |  | U16 | 3 | 1 | 1
13243 | Sag Coount |  |  | U16 | 3 | 1 | 1
13244 | Swell Count |  |  | U16 | 3 | 1 | 1
13245 |  |  |  | U16 | 3 | 1 | 1
13246 |  |  |  | U16 | 3 | 1 | 1
13247 |  |  |  | U16 | 3 | 1 | 1
13248 |  |  |  | U16 | 3 | 1 | 1
13249 |  |  |  | U16 | 3 | 1 | 1
Wave Sample
13250 | Wave Form V1 (160 sample) |  |  | S16 | 3 | 1 | 160
13410 | Wave Form V2 (160 sample) |  |  | S16 | 3 | 1 | 160
13570 | Wave Form V3 (160 sample) |  |  | S16 | 3 | 1 | 160
13730 | Wave Form V12 (160 sample) |  |  | S16 | 3 | 1 | 160
13890 | Wave Form V23 (160 sample) |  |  | S16 | 3 | 1 | 160
14050 | Wave Form V31 (160 sample) |  |  | S16 | 3 | 1 | 160
14210 | Wave Form I1 (160 sample) |  |  | S16 | 3 | 1 | 160
14370 | Wave Form I2 (160 sample) |  |  | S16 | 3 | 1 | 160
14530 | Wave Form I3 (160 sample) |  |  | S16 | 3 | 1 | 160
14690 | vscale |  |  | float | 3 | 2 | 1
14692 | iscale |  |  | float | 3 | 2 | 1
14694 |  |  |  | S16 | 3 | 1 | 6
월간리포트 생성위한 10분 평균
14700 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
14702 | U1 |  |  | float | 3 | 2 | 1
14704 | U2 |  |  | float | 3 | 2 | 1
14706 | U3 |  |  | float | 3 | 2 | 1
14708 | U THD1 |  |  | float | 3 | 2 | 1
14710 | U THD2 |  |  | float | 3 | 2 | 1
14712 | U THD3 |  |  | float | 3 | 2 | 1
14714 | Upp THD1 |  |  | float | 3 | 2 | 1
14716 | Upp THD2 |  |  | float | 3 | 2 | 1
14718 | Upp THD3 |  |  | float | 3 | 2 | 1
14720 | U Unbal Uu |  |  | float | 3 | 2 | 1
14722 | U Unbal Uo |  |  | float | 3 | 2 | 1
14724 | I1 |  |  | float | 3 | 2 | 1
14726 | I2 |  |  | float | 3 | 2 | 1
14728 | I3 |  |  | float | 3 | 2 | 1
14730 | In |  |  | float | 3 | 2 | 1
14732 | I THD1 |  |  | float | 3 | 2 | 1
14734 | I THD2 |  |  | float | 3 | 2 | 1
14736 | I THD3 |  |  | float | 3 | 2 | 1
14738 | I TDD1 |  |  | float | 3 | 2 | 1
14740 | I TDD2 |  |  | float | 3 | 2 | 1
14742 | I TDD3 |  |  | float | 3 | 2 | 1
14744 | K-factor 1 |  |  | float | 3 | 2 | 1
14746 | K-factor 2 |  |  | float | 3 | 2 | 1
14748 | K-factor 3 |  |  | float | 3 | 2 | 1
14750 | I Unbal Iu |  |  | float | 3 | 2 | 1
14752 | I Unbal Io |  |  | float | 3 | 2 | 1
14754 | kw imp |  |  | float | 3 | 2 | 1
14756 | kw exp |  |  | float | 3 | 2 | 1
14758 | kvar lag |  |  | float | 3 | 2 | 1
14760 | kvar lead |  |  | float | 3 | 2 | 1
14762 | kVA |  |  | float | 3 | 2 | 1
14764 | PF |  |  | float | 3 | 2 | 1
14766 | dPF |  |  | float | 3 | 2 | 1
14768 | temperature #1 |  |  | float | 3 | 2 | 1
14770 | temperature #2 |  |  | float | 3 | 2 | 1
14772 | temperature #3 |  |  | float | 3 | 2 | 1
14774 | temperature #4 |  |  | float | 3 | 2 | 1
14776 | temperature #5 |  |  | float | 3 | 2 | 1
14778 | Harmonics V1 |  |  | S16 | 3 | 1 | 24
14802 | Harmonics V2 |  |  | S16 | 3 | 1 | 24
14826 | Harmonics V3 |  |  | S16 | 3 | 1 | 24
14850 | Harmonics V12 |  |  | S16 | 3 | 1 | 24
14874 | Harmonics V23 |  |  | S16 | 3 | 1 | 24
14898 | Harmonics V31 |  |  | S16 | 3 | 1 | 24
14922 | Harmonics I1 |  |  | S16 | 3 | 1 | 24
14946 | Harmonics I2 |  |  | S16 | 3 | 1 | 24
14970 | Harmonics I3 |  |  | S16 | 3 | 1 | 24
14994 |  |  |  | U16 | 3 | 1 | 6
Energy log
15000 | Time Stamp |  |  | UTC | 3 | 2 | 1
15002 | kwh import |  |  | float | 3 | 2 | 1
15004 | kvarh lag |  |  | float | 3 | 2 | 1
15006 | kvarh lead |  |  | float | 3 | 2 | 1
15008 | kVAh |  |  | float | 3 | 2 | 1
15010 | energy log last day 01h |  |  | float | 3 | 2 | 4
15018 | energy log last day 02h |  |  | float | 3 | 2 | 4
15026 | energy log last day 03h |  |  | float | 3 | 2 | 4
15034 | energy log last day 04h |  |  | float | 3 | 2 | 4
15042 | energy log last day 05h |  |  | float | 3 | 2 | 4
15050 | energy log last day 06h |  |  | float | 3 | 2 | 4
15058 | energy log last day 07h |  |  | float | 3 | 2 | 4
15066 | energy log last day 08h |  |  | float | 3 | 2 | 4
15074 | energy log last day 09h |  |  | float | 3 | 2 | 4
15082 | energy log last day 10h |  |  | float | 3 | 2 | 4
15090 | energy log last day 11h |  |  | float | 3 | 2 | 4
15098 | energy log last day 12h |  |  | float | 3 | 2 | 4
15106 | energy log last day 13h |  |  | float | 3 | 2 | 4
15114 | energy log last day 14h |  |  | float | 3 | 2 | 4
15122 | energy log last day 15h |  |  | float | 3 | 2 | 4
15130 | energy log last day 16h |  |  | float | 3 | 2 | 4
15138 | energy log last day 17h |  |  | float | 3 | 2 | 4
15146 | energy log last day 18h |  |  | float | 3 | 2 | 4
15154 | energy log last day 19h |  |  | float | 3 | 2 | 4
15162 | energy log last day 20h |  |  | float | 3 | 2 | 4
15170 | energy log last day 21h |  |  | float | 3 | 2 | 4
15178 | energy log last day 22h |  |  | float | 3 | 2 | 4
15186 | energy log last day 23h |  |  | float | 3 | 2 | 4
15194 |  |  |  | U16 | 3 | 1 | 6
15200 | Time Stamp |  |  | UTC | 3 | 2 | 1
15202 | kwh import |  |  | float | 3 | 2 | 1
15204 | kvarh lag |  |  | float | 3 | 2 | 1
15206 | kvarh lead |  |  | float | 3 | 2 | 1
15208 | kVAh |  |  | float | 3 | 2 | 1
15210 | energy log this day 01h |  |  | float | 3 | 2 | 4
15218 | energy log this day 02h |  |  | float | 3 | 2 | 4
15226 | energy log this day 03h |  |  | float | 3 | 2 | 4
15234 | energy log this day 04h |  |  | float | 3 | 2 | 4
15242 | energy log this day 05h |  |  | float | 3 | 2 | 4
15250 | energy log this day 06h |  |  | float | 3 | 2 | 4
15258 | energy log this day 07h |  |  | float | 3 | 2 | 4
15266 | energy log this day 08h |  |  | float | 3 | 2 | 4
15274 | energy log this day 09h |  |  | float | 3 | 2 | 4
15282 | energy log this day 10h |  |  | float | 3 | 2 | 4
15290 | energy log this day 11h |  |  | float | 3 | 2 | 4
15298 | energy log this day 12h |  |  | float | 3 | 2 | 4
15306 | energy log this day 13h |  |  | float | 3 | 2 | 4
15314 | energy log this day 14h |  |  | float | 3 | 2 | 4
15322 | energy log this day 15h |  |  | float | 3 | 2 | 4
15330 | energy log this day 16h |  |  | float | 3 | 2 | 4
15338 | energy log this day 17h |  |  | float | 3 | 2 | 4
15346 | energy log this day 18h |  |  | float | 3 | 2 | 4
15354 | energy log this day 19h |  |  | float | 3 | 2 | 4
15362 | energy log this day 20h |  |  | float | 3 | 2 | 4
15370 | energy log this day 21h |  |  | float | 3 | 2 | 4
15378 | energy log this day 22h |  |  | float | 3 | 2 | 4
15386 | energy log this day 23h |  |  | float | 3 | 2 | 4
15394 |  |  |  | U16 | 3 | 1 | 6
demand log last day
15400 | Time Stamp |  |  | U32 | 3 | 2 | 1
15402 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
15594 |  |  |  | U16 | 3 | 1 | 6
ITIC
15600 | fr |  |  | U16 | 3 | 1 | 1
15601 | re |  |  | U16 | 3 | 1 | 1
15602 | count |  |  | U16 | 3 | 1 | 1
15603 | SEQ |  |  | U16 | 3 | 1 | 1
15604 | Log #1 | start ts |  | UTC | 3 | 2 | 1
15606 |  | start ts(ms) |  | U16 | 3 | 1 | 1
15607 |  | duration |  | U16 | 3 | 1 | 1
15608 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
15609 |  | mask |  | U16 | 3 | 1 | 1
15610 |  | Level 1 |  | float | 3 | 2 | 1
15612 |  | Level 2 |  | float | 3 | 2 | 1
15614 |  | Level 3 |  | float | 3 | 2 | 1
15616 |  | Normal |  | float | 3 | 2 | 1
15618 | Log #2 |  |  | U16 | 3 | 1 | 14
15632 | Log #3 |  |  | U16 | 3 | 1 | 14
15646 | Log #4 |  |  | U16 | 3 | 1 | 14
15660 | Log #5 |  |  | U16 | 3 | 1 | 14
15674 | Log #6 |  |  | U16 | 3 | 1 | 14
15688 | Log #7 |  |  | U16 | 3 | 1 | 14
15702 | Log #8 |  |  | U16 | 3 | 1 | 14
15716 | Log #9 |  |  | U16 | 3 | 1 | 14
15730 | Log #10 |  |  | U16 | 3 | 1 | 14
15744 | Log #11 |  |  | U16 | 3 | 1 | 14
15758 | Log #12 |  |  | U16 | 3 | 1 | 14
15772 | Log #13 |  |  | U16 | 3 | 1 | 14
15786 | Log #14 |  |  | U16 | 3 | 1 | 14
15800 | Log #15 |  |  | U16 | 3 | 1 | 14
15814 | Log #16 |  |  | U16 | 3 | 1 | 14
15828 | Log #17 |  |  | U16 | 3 | 1 | 14
15842 | Log #18 |  |  | U16 | 3 | 1 | 14
15856 | Log #19 |  |  | U16 | 3 | 1 | 14
15870 | Log #20 |  |  | U16 | 3 | 1 | 14
15884 | Log #21 |  |  | U16 | 3 | 1 | 14
15898 | Log #22 |  |  | U16 | 3 | 1 | 14
15912 | Log #23 |  |  | U16 | 3 | 1 | 14
15926 | Log #24 |  |  | U16 | 3 | 1 | 14
15940 | Log #25 |  |  | U16 | 3 | 1 | 14
15954 | Log #26 |  |  | U16 | 3 | 1 | 14
15968 | Log #27 |  |  | U16 | 3 | 1 | 14
15982 | Log #28 |  |  | U16 | 3 | 1 | 14
15996 | Log #29 |  |  | U16 | 3 | 1 | 14
16010 | Log #30 |  |  | U16 | 3 | 1 | 14
16024 | Log #31 |  |  | U16 | 3 | 1 | 14
16038 | Log #32 |  |  | U16 | 3 | 1 | 14
16052 |  |  |  | U16 | 3 | 1 | 8
ITIC(Configurator)
16060 | fr |  |  | U16 | 3 | 1 | 1
16061 | re |  |  | U16 | 3 | 1 | 1
16062 | count |  |  | U16 | 3 | 1 | 1
16063 | reserved |  |  | U16 | 3 | 1 | 1
16064 | Log #1 | start ts |  | UTC | 3 | 2 | 1
16066 |  | start ts(ms) |  | U16 | 3 | 1 | 1
16067 |  | duration |  | U16 | 3 | 1 | 1
16068 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
16069 |  | mask |  | U16 | 3 | 1 | 1
16070 |  | Level 1 |  | float | 3 | 2 | 1
16072 |  | Level 2 |  | float | 3 | 2 | 1
16074 |  | Level 3 |  | float | 3 | 2 | 1
16076 |  | Normal |  | float | 3 | 2 | 1
16078 | Log #2 |  |  | U16 | 3 | 1 | 14
16092 | Log #3 |  |  | U16 | 3 | 1 | 14
16106 | Log #4 |  |  | U16 | 3 | 1 | 14
16120 | Log #5 |  |  | U16 | 3 | 1 | 14
16134 | Log #6 |  |  | U16 | 3 | 1 | 14
16148 | Log #7 |  |  | U16 | 3 | 1 | 14
16162 | Log #8 |  |  | U16 | 3 | 1 | 14
16176 | Log #9 |  |  | U16 | 3 | 1 | 14
16190 | Log #10 |  |  | U16 | 3 | 1 | 14
16204 | Log #11 |  |  | U16 | 3 | 1 | 14
16218 | Log #12 |  |  | U16 | 3 | 1 | 14
16232 | Log #13 |  |  | U16 | 3 | 1 | 14
16246 | Log #14 |  |  | U16 | 3 | 1 | 14
16260 | Log #15 |  |  | U16 | 3 | 1 | 14
16274 | Log #16 |  |  | U16 | 3 | 1 | 14
16288 | Log #17 |  |  | U16 | 3 | 1 | 14
16302 | Log #18 |  |  | U16 | 3 | 1 | 14
16316 | Log #19 |  |  | U16 | 3 | 1 | 14
16330 | Log #20 |  |  | U16 | 3 | 1 | 14
16344 | Log #21 |  |  | U16 | 3 | 1 | 14
16358 | Log #22 |  |  | U16 | 3 | 1 | 14
16372 | Log #23 |  |  | U16 | 3 | 1 | 14
16386 | Log #24 |  |  | U16 | 3 | 1 | 14
16400 | Log #25 |  |  | U16 | 3 | 1 | 14
16414 | Log #26 |  |  | U16 | 3 | 1 | 14
16428 | Log #27 |  |  | U16 | 3 | 1 | 14
16442 | Log #28 |  |  | U16 | 3 | 1 | 14
16456 | Log #29 |  |  | U16 | 3 | 1 | 14
16470 | Log #30 |  |  | U16 | 3 | 1 | 14
16484 | Log #31 |  |  | U16 | 3 | 1 | 14
16498 | Log #32 |  |  | U16 | 3 | 1 | 14
16512 |  |  |  | U16 | 3 | 1 | 8
Setting 영역 시작
PQ Event
16520 | OC Level | 정격의 2배 |  | U16 | 3,16 | 1 | 1
16521 | OC Cycle | unused |  | U16 | 3,16 | 1 | 1
16522 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
16523 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
16524 |  |  |  | U16 | 3,16 | 1 | 2
16526 | Sag Level(%), 90% | < 90% |  | U16 | 3,16 | 1 | 1
16527 | Sag Cycle | unused |  | U16 | 3,16 | 1 | 1
16528 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
16529 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
16530 |  |  |  | U16 | 3,16 | 1 | 2
16532 | Swell Level(%), 110~200~ | > 110% |  | U16 | 3,16 | 1 | 1
16533 | Swell Cycle | unused |  | U16 | 3,16 | 1 | 1
16534 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
16535 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
16536 |  |  |  | U16 | 3,16 | 1 | 2
16538 | Interruption Level, 5% | < 5% |  | U16 | 3,16 | 1 | 1
16539 | Interruption Time, 60s | unused |  | U16 | 3,16 | 1 | 1
16540 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
16541 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
16542 |  |  |  | U16 | 3,16 | 1 | 2
Transient Trigger
16544 | Transient Voltage, HoldOff Time, 20ms | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
16545 | Transient Voltage, Absolute Peak Level, 200% | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
16546 | Transient Voltage, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
16547 | Transient Voltage, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
16548 | Transient Current, HoldOff Time | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
16549 | Transient Current, Absolute Peak Level | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
16550 | Transient Current, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
16551 | Transient Current, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
16552 |  |  |  | U16 | 3,16 | 1 | 12
Recorder
Waveform
16564 | Recorder resolution(32k, 8k) |  |  | U16 | 3,16 | 1 | 1
16565 | Recorded paramater (U or I) |  |  | U16 | 3,16 | 1 | 1
16566 | pre trigger time(0.1s) |  |  | U16 | 3,16 | 1 | 1
16567 | post trigger time(1s) |  |  | U16 | 3,16 | 1 | 1
Disturbance
16568 | Recorder resolution (Half Cycle) |  |  | U16 | 3,16 | 1 | 1
16569 | Recorded parametrs(U or I) |  |  | U16 | 3,16 | 1 | 1
16570 | pre trigger time(100 sample) |  |  | U16 | 3,16 | 1 | 1
16571 | post trigger time(900 sample) |  |  | U16 | 3,16 | 1 | 1
16572 |  |  |  | U16 | 3,16 | 1 | 12
Trend Recorder
16584 | Trend Group #1 Active |  |  | U16 | 3,16 | 1 | 1
16585 | Trend Group #1 Storage Interval |  |  | U16 | 3,16 | 1 | 1
16586 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
16587 | Trend Group #1, Channel #1 |  |  | U16 | 3,16 | 1 | 1
16588 | Trend Group #1, Channel #2 |  |  | U16 | 3,16 | 1 | 1
16589 | Trend Group #1, Channel #3 |  |  | U16 | 3,16 | 1 | 1
16590 | Trend Group #1, Channel #4 |  |  | U16 | 3,16 | 1 | 1
16591 | Trend Group #1, Channel #5 |  |  | U16 | 3,16 | 1 | 1
16592 | Trend Group #1, Channel #6 |  |  | U16 | 3,16 | 1 | 1
16593 | Trend Group #1, Channel #7 |  |  | U16 | 3,16 | 1 | 1
16594 | Trend Group #1, Channel #8 |  |  | U16 | 3,16 | 1 | 1
16595 | Trend Group #1, Channel #9 |  |  | U16 | 3,16 | 1 | 1
16596 | Trend Group #1, Channel #10 |  |  | U16 | 3,16 | 1 | 1
16597 | Trend Group #1, Channel #11 |  |  | U16 | 3,16 | 1 | 1
16598 | Trend Group #1, Channel #12 |  |  | U16 | 3,16 | 1 | 1
16599 | Trend Group #1, Channel #13 |  |  | U16 | 3,16 | 1 | 1
16600 | Trend Group #1, Channel #14 |  |  | U16 | 3,16 | 1 | 1
16601 | Trend Group #1, Channel #15 |  |  | U16 | 3,16 | 1 | 1
16602 | Trend Group #1, Channel #16 |  |  | U16 | 3,16 | 1 | 1
16603 | Trend Group #2 Active |  |  | U16 | 3,16 | 1 | 1
16604 | Trend Group #2 Storage Interval |  |  | U16 | 3,16 | 1 | 1
16605 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
16606 | Trend Group #2, Channel #1 |  |  | U16 | 3,16 | 1 | 1
16607 | Trend Group #2, Channel #2 |  |  | U16 | 3,16 | 1 | 1
16608 | Trend Group #2, Channel #3 |  |  | U16 | 3,16 | 1 | 1
16609 | Trend Group #2, Channel #4 |  |  | U16 | 3,16 | 1 | 1
16610 | Trend Group #2, Channel #5 |  |  | U16 | 3,16 | 1 | 1
16611 | Trend Group #2, Channel #6 |  |  | U16 | 3,16 | 1 | 1
16612 | Trend Group #2, Channel #7 |  |  | U16 | 3,16 | 1 | 1
16613 | Trend Group #2, Channel #8 |  |  | U16 | 3,16 | 1 | 1
16614 | Trend Group #2, Channel #9 |  |  | U16 | 3,16 | 1 | 1
16615 | Trend Group #2, Channel #10 |  |  | U16 | 3,16 | 1 | 1
16616 | Trend Group #2, Channel #11 |  |  | U16 | 3,16 | 1 | 1
16617 | Trend Group #2, Channel #12 |  |  | U16 | 3,16 | 1 | 1
16618 | Trend Group #2, Channel #13 |  |  | U16 | 3,16 | 1 | 1
16619 | Trend Group #2, Channel #14 |  |  | U16 | 3,16 | 1 | 1
16620 | Trend Group #2, Channel #15 |  |  | U16 | 3,16 | 1 | 1
16621 | Trend Group #2, Channel #16 |  |  | U16 | 3,16 | 1 | 1
16622 | Trend Group #3 Active |  |  | U16 | 3,16 | 1 | 1
16623 | Trend Group #3 Storage Interval |  |  | U16 | 3,16 | 1 | 1
16624 |  |  |  | U16 | 3,16 | 1 | 1
16625 | Trend Group #3, Channel #1 |  |  | U16 | 3,16 | 1 | 1
16626 | Trend Group #3, Channel #2 |  |  | U16 | 3,16 | 1 | 1
16627 | Trend Group #3, Channel #3 |  |  | U16 | 3,16 | 1 | 1
16628 | Trend Group #3, Channel #4 |  |  | U16 | 3,16 | 1 | 1
16629 | Trend Group #3, Channel #5 |  |  | U16 | 3,16 | 1 | 1
16630 | Trend Group #3, Channel #6 |  |  | U16 | 3,16 | 1 | 1
16631 | Trend Group #3, Channel #7 |  |  | U16 | 3,16 | 1 | 1
16632 | Trend Group #3, Channel #8 |  |  | U16 | 3,16 | 1 | 1
16633 | Trend Group #3, Channel #9 |  |  | U16 | 3,16 | 1 | 1
16634 | Trend Group #3, Channel #10 |  |  | U16 | 3,16 | 1 | 1
16635 | Trend Group #3, Channel #11 |  |  | U16 | 3,16 | 1 | 1
16636 | Trend Group #3, Channel #12 |  |  | U16 | 3,16 | 1 | 1
16637 | Trend Group #3, Channel #13 |  |  | U16 | 3,16 | 1 | 1
16638 | Trend Group #3, Channel #14 |  |  | U16 | 3,16 | 1 | 1
16639 | Trend Group #3, Channel #15 |  |  | U16 | 3,16 | 1 | 1
16640 | Trend Group #3, Channel #16 |  |  | U16 | 3,16 | 1 | 1
16641 | Trend Group #4 Active |  |  | U16 | 3,16 | 1 | 1
16642 | Trend Group #4 Storage Interval |  |  | U16 | 3,16 | 1 | 1
16643 |  |  |  | U16 | 3,16 | 1 | 1
16644 | Trend Group #4, Channel #1 |  |  | U16 | 3,16 | 1 | 1
16645 | Trend Group #4, Channel #2 |  |  | U16 | 3,16 | 1 | 1
16646 | Trend Group #4, Channel #3 |  |  | U16 | 3,16 | 1 | 1
16647 | Trend Group #4, Channel #4 |  |  | U16 | 3,16 | 1 | 1
16648 | Trend Group #4, Channel #5 |  |  | U16 | 3,16 | 1 | 1
16649 | Trend Group #4, Channel #6 |  |  | U16 | 3,16 | 1 | 1
16650 | Trend Group #4, Channel #7 |  |  | U16 | 3,16 | 1 | 1
16651 | Trend Group #4, Channel #8 |  |  | U16 | 3,16 | 1 | 1
16652 | Trend Group #4, Channel #9 |  |  | U16 | 3,16 | 1 | 1
16653 | Trend Group #4, Channel #10 |  |  | U16 | 3,16 | 1 | 1
16654 | Trend Group #4, Channel #11 |  |  | U16 | 3,16 | 1 | 1
16655 | Trend Group #4, Channel #12 |  |  | U16 | 3,16 | 1 | 1
16656 | Trend Group #4, Channel #13 |  |  | U16 | 3,16 | 1 | 1
16657 | Trend Group #4, Channel #14 |  |  | U16 | 3,16 | 1 | 1
16658 | Trend Group #4, Channel #15 |  |  | U16 | 3,16 | 1 | 1
16659 | Trend Group #4, Channel #16 |  |  | U16 | 3,16 | 1 | 1
16660 |  |  |  | U16 | 3,16 | 1 | 4
Power Quality Report
16664 | Active |  |  | U16 | 3,16 | 1 | 1
16665 | Start Day |  |  | U16 | 3,16 | 1 | 1
16666 |  |  |  | U16 |  | 1 | 8
Alarm Definition
16674 | compare Time Delay(1s) |  |  | U16 | 3,16 | 1 | 1
16675 |  |  |  | U16 |  | 1 | 1
16676 |  |  |  | U16 |  | 1 | 1
16677 |  |  |  | U16 |  | 1 | 1
Alarm Settings
16678 | Alarm Info #1 Channel(0:disabled, >0: enabled) |  |  | U16 | 3,16 | 1 | 1
16679 | Alarm Cond (0: < , 1:>) |  |  | U16 | 3,16 | 1 | 1
16680 | Hysteresis (% of Nominal) |  |  | U16 | 3,16 | 1 | 1
16681 | Alarm Action (None, Relay or Beep) |  |  | U16 | 3,16 | 1 | 1
16682 | Alarm Level |  |  | float | 3,16 | 2 | 1
16684 | Alarm Settings #2 |  |  | U16 | 3,16 | 1 | 6
16690 | Alarm Settings #3 |  |  | U16 | 3,16 | 1 | 6
16696 | Alarm Settings #4 |  |  | U16 | 3,16 | 1 | 6
16702 | Alarm Settings #5 |  |  | U16 | 3,16 | 1 | 6
16708 | Alarm Settings #6 |  |  | U16 | 3,16 | 1 | 6
16714 | Alarm Settings #7 |  |  | U16 | 3,16 | 1 | 6
16720 | Alarm Settings #8 |  |  | U16 | 3,16 | 1 | 6
16726 | Alarm Settings #9 |  |  | U16 | 3,16 | 1 | 6
16732 | Alarm Settings #10 |  |  | U16 | 3,16 | 1 | 6
16738 | Alarm Settings #11 |  |  | U16 | 3,16 | 1 | 6
16744 | Alarm Settings #12 |  |  | U16 | 3,16 | 1 | 6
16750 | Alarm Settings #13 |  |  | U16 | 3,16 | 1 | 6
16756 | Alarm Settings #14 |  |  | U16 | 3,16 | 1 | 6
16762 | Alarm Settings #15 |  |  | U16 | 3,16 | 1 | 6
16768 | Alarm Settings #16 |  |  | U16 | 3,16 | 1 | 6
16774 | Alarm Settings #17 |  |  | U16 | 3,16 | 1 | 6
16780 | Alarm Settings #18 |  |  | U16 | 3,16 | 1 | 6
16786 | Alarm Settings #19 |  |  | U16 | 3,16 | 1 | 6
16792 | Alarm Settings #20 |  |  | U16 | 3,16 | 1 | 6
16798 | Alarm Settings #21 |  |  | U16 | 3,16 | 1 | 6
16804 | Alarm Settings #22 |  |  | U16 | 3,16 | 1 | 6
16810 | Alarm Settings #23 |  |  | U16 | 3,16 | 1 | 6
16816 | Alarm Settings #24 |  |  | U16 | 3,16 | 1 | 6
16822 | Alarm Settings #25 |  |  | U16 | 3,16 | 1 | 6
16828 | Alarm Settings #26 |  |  | U16 | 3,16 | 1 | 6
16834 | Alarm Settings #27 |  |  | U16 | 3,16 | 1 | 6
16840 | Alarm Settings #28 |  |  | U16 | 3,16 | 1 | 6
16846 | Alarm Settings #29 |  |  | U16 | 3,16 | 1 | 6
16852 | Alarm Settings #30 |  |  | U16 | 3,16 | 1 | 6
16858 | Alarm Settings #31 |  |  | U16 | 3,16 | 1 | 6
16864 | Alarm Settings #32 |  |  | U16 | 3,16 | 1 | 6

## #3CH modbus
address | name | 설명 | Unit | TYPE | FC | Word Count | Item Count
Metering
20000 | Time Stamp |  |  | UTC | 3 | 2 | 1
20002 | TYPE |  |  | U16 | 3 | 1 | 1
20003 | STATUS | 1 : online, 0 : offline |  | U16 | 3 | 1 | 1
20004 | Frequency | 라인주파수 | Hz | float | 3 | 2 | 1
20006 | Internal Temp |  | ℃ | float | 3 | 2 | 1
20008 | U1 | 상전압 1 | V | float | 3 | 2 | 1
20010 | U2 | 상전압 2 |  | float | 3 | 2 | 1
20012 | U3 | 상전압 3 |  | float | 3 | 2 | 1
20014 | U~ | 상전압 평균 |  | float | 3 | 2 | 1
20016 | U12 | 선간 전압 12 |  | float | 3 | 2 | 1
20018 | U23 | 선간 전압 23 |  | float | 3 | 2 | 1
20020 | U31 | 선간 전압 31 |  | float | 3 | 2 | 1
20022 | Upp~ | 선간 전압 평균 |  | float | 3 | 2 | 1
20024 | Uunbalance2 |  | % | float | 3 | 2 | 1
20026 | Uunbalance0 |  |  | float | 3 | 2 | 1
20028 | U Zero Sequence Mag. |  |  | float | 3 | 2 | 1
20030 | U Zero Sequence angle |  |  | float | 3 | 2 | 1
20032 | U Positive Sequence Mag. |  |  | float | 3 | 2 | 1
20034 | U Positive Sequence angle |  |  | float | 3 | 2 | 1
20036 | U Negative Sequence Mag |  |  | float | 3 | 2 | 1
20038 | U Negative Sequence angle |  |  | float | 3 | 2 | 1
20040 | Angle U1 |  |  | float | 3 | 2 | 1
20042 | Angle U2 |  |  | float | 3 | 2 | 1
20044 | Angle U3 |  |  | float | 3 | 2 | 1
20046 | U Underdeviation L1 |  | % | float | 3 | 2 | 1
20048 | U Underdeviation L2 |  | % | float | 3 | 2 | 1
20050 | U Underdeviation L3 |  | % | float | 3 | 2 | 1
20052 | U Overdeviation L1 |  | % | float | 3 | 2 | 1
20054 | U Overdeviation L2 |  | % | float | 3 | 2 | 1
20056 | U Overdeviation L3 |  | % | float | 3 | 2 | 1
20058 | I1 | 상전류 1 | A | float | 3 | 2 | 1
20060 | I2 | 상전류 2 |  | float | 3 | 2 | 1
20062 | I3 | 상전류 3 |  | float | 3 | 2 | 1
20064 | I~ |  |  | float | 3 | 2 | 1
20066 | I total (I1+I2+I3) |  |  | float | 3 | 2 | 1
20068 | In(Measured) |  |  | float | 3 | 2 | 1 | 1. 5A: -3P4W(In) -3P3W(Ig), 2. AT/VT: Ig로 사용
20070 | In(Calculated) | Ia+Ib+Ic+In = Ig |  | float | 3 | 2 | 1 | 1. 5A: -3P4W(Ig=Ia+Ib+Ic+In), -3P3W(Ig=Ia+Ib+Ic), 2. AT/VT: 5A와 동일
20072 | Ig |  |  | float | 3 | 2 | 1
20074 | I Zero Sequence Mag |  |  | float | 3 | 2 | 1
20076 | I Zero Sequence angle |  |  | float | 3 | 2 | 1
20078 | I Positive Sequence Mag. |  |  | float | 3 | 2 | 1
20080 | I Positive Sequence angle |  |  | float | 3 | 2 | 1
20082 | I Negative Sequence Mag. |  |  | float | 3 | 2 | 1
20084 | I Negative Sequence angle |  |  | float | 3 | 2 | 1
20086 | Angle I1 |  |  | float | 3 | 2 | 1
20088 | Angle I2 |  |  | float | 3 | 2 | 1
20090 | Angle I3 |  |  | float | 3 | 2 | 1
20092 | Iunbalance2 |  | % | float | 3 | 2 | 1
20094 | Iunbalance0 |  |  | float | 3 | 2 | 1
20096 | P1 | 유효전력 P1 | W | float | 3 | 2 | 1
20098 | P2 | 유효전력 P2 |  | float | 3 | 2 | 1
20100 | P3 | 유효전력 P3 |  | float | 3 | 2 | 1
20102 | P total | 유효전력 P-total |  | float | 3 | 2 | 1
20104 | fP1 |  |  | float | 3 | 2 | 1
20106 | fP2 |  |  | float | 3 | 2 | 1
20108 | fP3 |  |  | float | 3 | 2 | 1
20110 | fP total |  |  | float | 3 | 2 | 1
20112 | Q1 | 무효전력 Q1 | VAR | float | 3 | 2 | 1
20114 | Q2 | 무효전력 Q2 |  | float | 3 | 2 | 1
20116 | Q3 | 무효전력 Q3 |  | float | 3 | 2 | 1
20118 | Q total | 무효전력 Q-total |  | float | 3 | 2 | 1
20120 | fQ1 |  |  | float | 3 | 2 | 1
20122 | fQ2 |  |  | float | 3 | 2 | 1
20124 | fQ3 |  |  | float | 3 | 2 | 1
20126 | fQ total |  |  | float | 3 | 2 | 1
20128 | S1 | 피상전력 S1 | VA | float | 3 | 2 | 1
20130 | S2 | 피상전력 S2 |  | float | 3 | 2 | 1
20132 | S3 | 피상전력 S3 |  | float | 3 | 2 | 1
20134 | S total | 피상전력 S-total |  | float | 3 | 2 | 1
20136 | fS1 |  |  | float | 3 | 2 | 1
20138 | fS2 |  |  | float | 3 | 2 | 1
20140 | fS3 |  |  | float | 3 | 2 | 1
20142 | fS total |  |  | float | 3 | 2 | 1
20144 | PF1 | 역률 PF1 | % | float | 3 | 2 | 1
20146 | PF2 | 역률 PF2 |  | float | 3 | 2 | 1
20148 | PF3 | 역률 PF3 |  | float | 3 | 2 | 1
20150 | PF total | 역률 PF-total |  | float | 3 | 2 | 1
20152 | dPF1 |  | % | float | 3 | 2 | 1
20154 | dPF2 |  |  | float | 3 | 2 | 1
20156 | dPF3 |  |  | float | 3 | 2 | 1
20158 | dPF total |  |  | float | 3 | 2 | 1
20160 | deformed Power D L1 |  | W | float | 3 | 2 | 1 | S=sqrt {P^{2}+Q^{2}+D^{2}}
20162 | deformed Power D L2 |  |  | float | 3 | 2 | 1
20164 | deformed Power D L3 |  |  | float | 3 | 2 | 1
20166 | deformed Power D Total |  |  | float | 3 | 2 | 1
20168 | Power Angle(atan(fPt,fQt) L1 |  | Degree | float | 3 | 2 | 1 | Angle between fundamental phase voltage and phase current
20170 | Power Angle(atan(fPt,fQt) L2 |  |  | float | 3 | 2 | 1
20172 | Power Angle(atan(fPt,fQt) L3 |  |  | float | 3 | 2 | 1
20174 |  |  |  | float | 3 | 2 | 1
20176 | THD V1 |  | % | float | 3 | 2 | 1
20178 | THD V2 |  |  | float | 3 | 2 | 1 | Chip에서 제공하는 결과 사용
20180 | THD V3 |  |  | float | 3 | 2 | 1
20182 | THD V12 |  |  | float | 3 | 2 | 1
20184 | THD V23 |  |  | float | 3 | 2 | 1
20186 | THD V31 |  |  | float | 3 | 2 | 1
20188 | CF V1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
20190 | CF V2 |  |  | float | 3 | 2 | 1
20192 | CF V3 |  |  | float | 3 | 2 | 1
20194 | CF V12 |  |  | float | 3 | 2 | 1
20196 | CF V23 |  |  | float | 3 | 2 | 1
20198 | CF V31 |  |  | float | 3 | 2 | 1
20200 | THD I1 |  |  | float | 3 | 2 | 1
20202 | THD I2 |  |  | float | 3 | 2 | 1
20204 | THD I3 |  |  | float | 3 | 2 | 1
20206 | TDD I1 |  |  | float | 3 | 2 | 1
20208 | TDD I2 |  |  | float | 3 | 2 | 1
20210 | TDD I3 |  |  | float | 3 | 2 | 1
20212 | K I1 | K-FACTOR : 고조파 허용율 |  | float | 3 | 2 | 1
20214 | K I2 |  |  | float | 3 | 2 | 1
20216 | K I3 |  |  | float | 3 | 2 | 1
20218 | CF I1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
20220 | CF I2 |  |  | float | 3 | 2 | 1
20222 | CF I3 |  |  | float | 3 | 2 | 1
20224 | fU1 | 기본파 U1 | V | float | 3 | 2 | 1
20226 | fU2 | 기본파 U2 |  | float | 3 | 2 | 1
20228 | fU3 | 기본파 U3 |  | float | 3 | 2 | 1
20230 | fU~ | 기본파 전압 평균 |  | float | 3 | 2 | 1
20232 | fI1 | 기본파 I1 | A | float | 3 | 2 | 1
20234 | fI2 | 기본파 I2 |  | float | 3 | 2 | 1
20236 | fI3 | 기본파 I3 |  | float | 3 | 2 | 1
20238 | fI~ | 기본파 전류 평균 |  | float | 3 | 2 | 1
Energy
20240 | import kwh(0 ~ 999,999,999.9 kw) | 누적 유효전력량 |  | U32 | 3 | 2 | 1
20242 | export kwh |  |  | U32 | 3 | 2 | 1
20244 | import kvarh |  |  | U32 | 3 | 2 | 1
20246 | export kvarh |  |  | U32 | 3 | 2 | 1
20248 | kvah |  |  | U32 | 3 | 2 | 1
20250 |  |  |  | U32 | 3 | 2 | 1
20252 | import kwh this month |  |  | U32 | 3 | 2 | 1
20254 | export kwh this month |  |  | U32 | 3 | 2 | 1
20256 | import kvarh this month |  |  | U32 | 3 | 2 | 1
20258 | export kvarh this month |  |  | U32 | 3 | 2 | 1
20260 | kvah this month |  |  | U32 | 3 | 2 | 1
20262 |  |  |  | U32 | 3 | 2 | 1
20264 | import kwh last month |  |  | U32 | 3 | 2 | 1 | Demand P(import)
20266 | export kwh last month |  |  | U32 | 3 | 2 | 1
20268 | import kvarh last month |  |  | U32 | 3 | 2 | 1
20270 | export kvarh last month |  |  | U32 | 3 | 2 | 1
20272 | kvah last month |  |  | U32 | 3 | 2 | 1
20274 |  |  |  | U32 | 3 | 2 | 1
20276 | import kwh | 0~999,999,999.999 kw |  | U64 | 3 | 4 | 1 | Demand P(import)
20280 | export kwh |  |  | U64 | 3 | 4 | 1
20284 | import kvarh |  |  | U64 | 3 | 4 | 1
20288 | export kvarh |  |  | U64 | 3 | 4 | 1
20292 | kvah |  |  | U64 | 3 | 4 | 1
20296 |  |  |  | U64 | 3 | 4 | 1
Demand
20300 | Time Stamp |  |  | UTC | 3 | 2 | 1
20302 | Max Demand P(import) |  |  | float | 3 | 2 | 1
20304 | Time Stamp |  |  | UTC | 3 | 2 | 1
20306 | Max Demand P(export) |  |  | float | 3 | 2 | 1
20308 | Time Stamp |  |  | UTC | 3 | 2 | 1
20310 | Max Demand Q(import) |  |  | float | 3 | 2 | 1
20312 | Time Stamp |  |  | UTC | 3 | 2 | 1
20314 | Max Demand Q(export) |  |  | float | 3 | 2 | 1
20316 | Time Stamp |  |  | UTC | 3 | 2 | 1
20318 | Max Demand S |  |  | float | 3 | 2 | 1
20320 | Time Stamp |  |  | UTC | 3 | 2 | 1
20322 | Max Demand I1 |  |  | float | 3 | 2 | 1
20324 | Time Stamp |  |  | UTC | 3 | 2 | 1
20326 | Max Demand I2 |  |  | float | 3 | 2 | 1
20328 | Time Stamp |  |  | UTC | 3 | 2 | 1
20330 | Max Demand I3 |  |  | float | 3 | 2 | 1
20332 | Demand time stamp |  |  | UTC | 3 | 2 | 1
20334 | Demand P(import) |  |  | float | 3 | 2 | 1
20336 | Demand P(export) |  |  | float | 3 | 2 | 1 | 최근 24시간 그래프 그린다
20338 | Demand Q(import) |  |  | float | 3 | 2 | 1
20340 | Demand Q(export) |  |  | float | 3 | 2 | 1
20342 | Demand S(export) |  |  | float | 3 | 2 | 1
20344 | Demand I1 |  |  | float | 3 | 2 | 1
20346 | Demand I2 |  |  | float | 3 | 2 | 1
20348 | Demand I3 |  |  | float | 3 | 2 | 1
20350 | Present Demand P(import) |  |  | float | 3 | 2 | 1
20352 | Present Demand P(export) |  |  | float | 3 | 2 | 1
20354 | Present Demand Q(import) |  |  | float | 3 | 2 | 1
20356 | Present Demand Q(export) |  |  | float | 3 | 2 | 1
20358 | Present Demand S(export) |  |  | float | 3 | 2 | 1
20360 | Forecast Demand P(export) |  |  | float | 3 | 2 | 1
20362 | Demand P 15m(import) |  |  | float | 3 | 2 | 1
20364 |  |  |  | float | 3 | 2 | 1
20366 |  |  |  | float | 3 | 2 | 1
20368 | Time Stamp(Demand Log 시작일) |  |  | U32 | 3 | 2 | 1
20370 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
20562 |  |  |  | float | 3 | 2 | 19
Voltage Quality RealTime Value
20600 | Voltage Under Deviation L1 |  | % | float | 3 | 2 | 1
20602 | Voltage Under Deviation L2 |  | % | float | 3 | 2 | 1
20604 | Voltage Under Deviation L3 |  | % | float | 3 | 2 | 1
20606 | Voltage Under Value L1 |  | rms | float | 3 | 2 | 1
20608 | Voltage Under Value L2 |  | rms | float | 3 | 2 | 1
20610 | Voltage Under Value L3 |  | rms | float | 3 | 2 | 1
20612 | Voltage Over Deviation L1 |  | % | float | 3 | 2 | 1
20614 | Voltage Over Deviation L2 |  | % | float | 3 | 2 | 1
20616 | Voltage Over Deviation L3 |  | % | float | 3 | 2 | 1
20618 | Voltage Over Value L1 |  | rms | float | 3 | 2 | 1
20620 | Voltage Over Value L2 |  | rms | float | 3 | 2 | 1
20622 | Voltage Over Value L3 |  | rms | float | 3 | 2 | 1
20624 | Flickers Pi L1 | 150/180 Cycles |  | float | 3 | 2 | 1
20626 | Flickers Pi L2 |  |  | float | 3 | 2 | 1
20628 | Flickers Pi L3 |  |  | float | 3 | 2 | 1
20630 | Flicker Pst L1 | 10min |  | float | 3 | 2 | 1
20632 | Flicker Pst L2 |  |  | float | 3 | 2 | 1
20634 | Flicker Pst L3 |  |  | float | 3 | 2 | 1
20636 | Flicker Plt L1 | 2hr |  | float | 3 | 2 | 1 | 최근 24시간 그래프 그린다
20638 | Flicker Plt L2 |  |  | float | 3 | 2 | 1
20640 | Flicker Plt L3 |  |  | float | 3 | 2 | 1
20642 | Signaling Volt L1 | Magnitude of current 10/12 cycles as a percentage of nominal voltage. |  | float | 3 | 2 | 1
20644 | Signaling Volt L2 |  |  | float | 3 | 2 | 1
20646 | Signaling Volt L3 |  |  | float | 3 | 2 | 1
20648 | Signaling Volt Max L1 | Maximum magnitude of MSV from recording started as a percentage of nominal voltage |  | float | 3 | 2 | 1
20650 | Signaling Volt Max L2 |  |  | float | 3 | 2 | 1
20652 | Signaling Volt Max L3 |  |  | float | 3 | 2 | 1
20654 |  |  |  | float | 3 | 2 | 23
EN50160 This Week
20700 | start date |  |  | UTC | 3 | 2 | 1
20702 | end date |  |  | UTC | 3 | 2 | 1
20704 | status&compliance | bit 0: Freq Var1 bit 1: Freq Var2 bit 2: Volt Var1 L1 bit 3: Volt Var1 L2 bit 4: Volt Var1 L3 bit 5: Volt Var2 L1 bit 6: Volt Var2 L2 bit 7: Volt Var2 L3 bit 8: Unbalance bit 9: Volt THD L1 bit 10: Volt THD L2 bit 11: Volt THD L3 bit 12: Volt HD L1 bit 13: Volt HD L2 bit 14: Volt HD L3 bit 15: Pst L1 bit 16: Pst L2 bit 17: Pst L3 bit 18: Plt L1 bit 19: Plt L2 bit 20: Plt L3 bit 21: SigVolt L1 bit 22: SigVolt L2 bit 23: SigVolt L3 bit 31: Complete [status] 0: OK 1: failed |  | U32 | 3 | 2 | 1
20706 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1 | 95%/Week
20707 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1 | Info Only
20708 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
20709 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
20710 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
20711 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
20712 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
20713 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1 | Info Only
20714 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
20715 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
20716 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
20717 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
20718 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
20719 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
20720 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
20721 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
20722 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
20723 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
20724 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
20725 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
20726 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
20727 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
20728 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
20729 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
20730 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
20731 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1 | 99%/Day
20732 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
20733 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
20734 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
20735 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
20736 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
20737 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
20738 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
20739 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
20740 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
20741 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
20742 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
20743 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
20744 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
20745 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
20746 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
20747 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
20748 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
20749 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
EN50160 Last Week
20750 | start date |  |  | UTC | 3 | 2 | 1
20752 | end date |  |  | UTC | 3 | 2 | 1
20754 | status |  |  | U16 | 3 | 1 | 1
20755 | compilance |  |  | U16 | 3 | 1 | 1
20756 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1
20757 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1
20758 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
20759 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
20760 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1
20761 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
20762 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
20763 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1
20764 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
20765 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
20766 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1
20767 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
20768 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
20769 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1
20770 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
20771 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
20772 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1
20773 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
20774 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
20775 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1
20776 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
20777 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
20778 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1
20779 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
20780 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
20781 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1
20782 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
20783 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
20784 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
20785 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
20786 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
20787 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
20788 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
20789 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
20790 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
20791 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
20792 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
20793 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
20794 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
20795 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
20796 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
20797 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
20798 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
20799 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
Harmonics
20800 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
20864 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
20928 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
20992 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
21056 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
21120 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
21184 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
21248 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
21312 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
21376 |  |  |  | S16 | 3 | 1 | 24
Inter Harmonics
21400 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
21464 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
21528 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
21592 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
21656 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
21720 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
21784 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
21848 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
21912 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
21976 |  |  |  | S16 | 3 | 1 | 24
Max/Min
22000 | fr |  |  | U16 | 3 | 1 | 1
22001 | re |  |  | U16 | 3 | 1 | 1
22002 | Reset TimeStamp |  |  | UTC | 3 | 2 | 1
22004 | Frequency |  |  | float | 3 | 2 | 4
22012 | Temp |  |  | float | 3 | 2 | 4
22020 | U1 |  |  | float | 3 | 2 | 4
22028 | U2 |  |  | float | 3 | 2 | 4
22036 | U3 |  |  | float | 3 | 2 | 4 | http://www.relaytech.com/symcomp_calculator.htm
22044 | U~ |  |  | float | 3 | 2 | 4
22052 | U12 |  |  | float | 3 | 2 | 4
22060 | U23 |  |  | float | 3 | 2 | 4
22068 | U31 |  |  | float | 3 | 2 | 4
22076 | Upp~ |  |  | float | 3 | 2 | 4
22084 | I1 |  |  | float | 3 | 2 | 4
22092 | I2 |  |  | float | 3 | 2 | 4
22100 | I3 |  |  | float | 3 | 2 | 4
22108 | I~ |  |  | float | 3 | 2 | 4
22116 | I total |  |  | float | 3 | 2 | 4
22124 | In |  |  | float | 3 | 2 | 4
22132 | Isum |  |  | float | 3 | 2 | 4
22140 | P1 |  |  | float | 3 | 2 | 4
22148 | P2 |  |  | float | 3 | 2 | 4
22156 | P3 |  |  | float | 3 | 2 | 4
22164 | P total |  |  | float | 3 | 2 | 4
22172 | Q1 |  |  | float | 3 | 2 | 4
22180 | Q2 |  |  | float | 3 | 2 | 4
22188 | Q3 |  |  | float | 3 | 2 | 4
22196 | Q total |  |  | float | 3 | 2 | 4
22204 | S1 |  |  | float | 3 | 2 | 4
22212 | S2 |  |  | float | 3 | 2 | 4
22220 | S3 |  |  | float | 3 | 2 | 4
22228 | S total |  |  | float | 3 | 2 | 4
22236 | PF L1 |  |  | float | 3 | 2 | 4
22244 | PF L2 |  |  | float | 3 | 2 | 4
22252 | PF L3 |  |  | float | 3 | 2 | 4
22260 | PF total |  |  | float | 3 | 2 | 4
22268 | THD U1 |  |  | float | 3 | 2 | 4
22276 | THD U2 |  |  | float | 3 | 2 | 4
22284 | THD U3 |  |  | float | 3 | 2 | 4
22292 | THD U12 |  |  | float | 3 | 2 | 4
22300 | THD U23 |  |  | float | 3 | 2 | 4
22308 | THD U31 |  |  | float | 3 | 2 | 4
22316 | THD I1 |  |  | float | 3 | 2 | 4
22324 | THD I2 |  |  | float | 3 | 2 | 4
22332 | THD I3 |  |  | float | 3 | 2 | 4
22340 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
22342 | reserved |  |  | U16 | 3 | 1 | 1
22343 | CRC |  |  | U16 | 3 | 1 | 1
22344 |  |  |  | U16 | 3 | 1 | 6
alarm status
22350 | fr |  |  | U16 | 3 | 1 | 1
22351 | re |  |  | U16 | 3 | 1 | 1
22352 | reset Ts |  |  | UTC | 3 | 2 | 1
22354 | Alarm State #1 | Alarm Channel |  | U16 | 3 | 1 | 1
22355 |  | Alarm Condition |  | U16 | 3 | 1 | 1
22356 |  | Alarm Level |  | float | 3 | 2 | 1
22358 |  | Alarm Status |  | U16 | 3 | 1 | 1
22359 |  | Alarm Count |  | U16 | 3 | 1 | 1
22360 | Alarm State #2 |  |  | U16 | 3 | 1 | 6
22366 | Alarm State #3 |  |  | U16 | 3 | 1 | 6
22372 | Alarm State #4 |  |  | U16 | 3 | 1 | 6
22378 | Alarm State #5 |  |  | U16 | 3 | 1 | 6
22384 | Alarm State #6 |  |  | U16 | 3 | 1 | 6
22390 | Alarm State #7 |  |  | U16 | 3 | 1 | 6
22396 | Alarm State #8 |  |  | U16 | 3 | 1 | 6
22402 | Alarm State #9 |  |  | U16 | 3 | 1 | 6
22408 | Alarm State #10 |  |  | U16 | 3 | 1 | 6
22414 | Alarm State #11 |  |  | U16 | 3 | 1 | 6
22420 | Alarm State #12 |  |  | U16 | 3 | 1 | 6
22426 | Alarm State #13 |  |  | U16 | 3 | 1 | 6
22432 | Alarm State #14 |  |  | U16 | 3 | 1 | 6
22438 | Alarm State #15 |  |  | U16 | 3 | 1 | 6
22444 | Alarm State #16 |  |  | U16 | 3 | 1 | 6
22450 | Alarm State #17 |  |  | U16 | 3 | 1 | 6
22456 | Alarm State #18 |  |  | U16 | 3 | 1 | 6
22462 | Alarm State #19 |  |  | U16 | 3 | 1 | 6
22468 | Alarm State #20 |  |  | U16 | 3 | 1 | 6
22474 | Alarm State #21 |  |  | U16 | 3 | 1 | 6
22480 | Alarm State #22 |  |  | U16 | 3 | 1 | 6
22486 | Alarm State #23 |  |  | U16 | 3 | 1 | 6
22492 | Alarm State #24 |  |  | U16 | 3 | 1 | 6
22498 | Alarm State #25 |  |  | U16 | 3 | 1 | 6
22504 | Alarm State #26 |  |  | U16 | 3 | 1 | 6
22510 | Alarm State #27 |  |  | U16 | 3 | 1 | 6
22516 | Alarm State #28 |  |  | U16 | 3 | 1 | 6
22522 | Alarm State #29 |  |  | U16 | 3 | 1 | 6
22528 | Alarm State #30 |  |  | U16 | 3 | 1 | 6
22534 | Alarm State #31 |  |  | U16 | 3 | 1 | 6
22540 | Alarm State #32 |  |  | U16 | 3 | 1 | 6
22546 | update Ts |  |  | U32 | 3 | 2 | 1
22548 | Global Alarm Status | (alarm 하나라도 있으면 1, 아니면 0) |  | U16 | 3 | 1 | 1
22549 |  |  |  | U16 | 3 | 1 | 1
alarm log
22550 | fr | 0 ~ 1023 |  | U16 | 3 | 1 | 1
22551 | re | 0 ~ 1023 |  | U16 | 3 | 1 | 1
22552 | count | 전체 log 수 |  | U16 | 3 | 1 | 1
22553 | seq |  |  | U16 | 3 | 1 | 1
22554 | Alarm Log #1 | Time Stamp |  | UTC | 3 | 2 | 1 | 2019-5-11변경
22556 |  | status |  | U16 | 3 | 1 | 1
22557 |  | Alarm Channel & Condition |  | U16 | 3 | 1 | 1
22558 |  | level |  | float | 3 | 2 | 1
22560 |  | Value |  | float | 3 | 2 | 1
22562 | Alarm Log #2 |  |  | U16 | 3 | 1 | 8
22570 | Alarm Log #3 |  |  | U16 | 3 | 1 | 8
22578 | Alarm Log #4 |  |  | U16 | 3 | 1 | 8
22586 | Alarm Log #5 |  |  | U16 | 3 | 1 | 8
22594 | Alarm Log #6 |  |  | U16 | 3 | 1 | 8
22602 | Alarm Log #7 |  |  | U16 | 3 | 1 | 8
22610 | Alarm Log #8 |  |  | U16 | 3 | 1 | 8
22618 | Alarm Log #9 |  |  | U16 | 3 | 1 | 8
22626 | Alarm Log #10 |  |  | U16 | 3 | 1 | 8
22634 | Alarm Log #11 |  |  | U16 | 3 | 1 | 8
22642 | Alarm Log #12 |  |  | U16 | 3 | 1 | 8
22650 | Alarm Log #13 |  |  | U16 | 3 | 1 | 8
22658 | Alarm Log #14 |  |  | U16 | 3 | 1 | 8
22666 | Alarm Log #15 |  |  | U16 | 3 | 1 | 8
22674 | Alarm Log #16 |  |  | U16 | 3 | 1 | 8
22682 | Alarm Log #17 |  |  | U16 | 3 | 1 | 8
22690 | Alarm Log #18 |  |  | U16 | 3 | 1 | 8
22698 | Alarm Log #19 |  |  | U16 | 3 | 1 | 8
22706 | Alarm Log #20 |  |  | U16 | 3 | 1 | 8
22714 | Alarm Log #21 |  |  | U16 | 3 | 1 | 8
22722 | Alarm Log #22 |  |  | U16 | 3 | 1 | 8
22730 | Alarm Log #23 |  |  | U16 | 3 | 1 | 8
22738 | Alarm Log #24 |  |  | U16 | 3 | 1 | 8
22746 | Alarm Log #25 |  |  | U16 | 3 | 1 | 8
22754 | Alarm Log #26 |  |  | U16 | 3 | 1 | 8
22762 | Alarm Log #27 |  |  | U16 | 3 | 1 | 8
22770 | Alarm Log #28 |  |  | U16 | 3 | 1 | 8
22778 | Alarm Log #29 |  |  | U16 | 3 | 1 | 8
22786 | Alarm Log #30 |  |  | U16 | 3 | 1 | 8
22794 | Alarm Log #31 |  |  | U16 | 3 | 1 | 8
22802 | Alarm Log #32 |  |  | U16 | 3 | 1 | 8
22810 |  |  |  | U16 | 3 | 1 | 40
이벤트 리스트
22850 | fr | 0 ~ 1023 |  | U16 | 3 | 1 | 1
22851 | re | 0 ~ 1023 |  | U16 | 3 | 1 | 1
22852 | count | 0 ~ 1023 |  | U16 | 3 | 1 | 1
22853 | seq |  |  | U16 | 3 | 1 | 1
PQ 이벤트(Sag, Swell, Transient, OC)
22854 | start ts |  |  | UTC | 3 | 2 | 1
22856 | start ts(ms) |  |  | U16 | 3 | 1 | 1
22857 | duration |  |  | U16 | 3 | 1 | 1
22858 | type | 1 : E_SAG 2 : E_SWELL 3 : E_sINTR 4 : E_lINTR 5 : E_OC 6 : E_RVC 7 : E_TrV 8 : E_TrC |  | U16 | 3 | 1 | 1
22859 | mask |  |  | U16 | 3 | 1 | 1
22860 | Level 1 |  |  | float | 3 | 2 | 1
22862 | Level 2 |  |  | float | 3 | 2 | 1
22864 | Level 3 |  |  | float | 3 | 2 | 1
22866 | PQ Event #2 |  |  | U16 | 3 | 1 | 12
22878 | PQ Event #3 |  |  | U16 | 3 | 1 | 12
22890 | PQ Event #4 |  |  | U16 | 3 | 1 | 12
22902 | PQ Event #5 |  |  | U16 | 3 | 1 | 12
22914 | PQ Event #6 |  |  | U16 | 3 | 1 | 12
22926 | PQ Event #7 |  |  | U16 | 3 | 1 | 12
22938 | PQ Event #8 |  |  | U16 | 3 | 1 | 12
22950 | PQ Event #9 |  |  | U16 | 3 | 1 | 12
22962 | PQ Event #10 |  |  | U16 | 3 | 1 | 12
22974 | PQ Event #11 |  |  | U16 | 3 | 1 | 12
22986 | PQ Event #12 |  |  | U16 | 3 | 1 | 12
22998 | PQ Event #13 |  |  | U16 | 3 | 1 | 12
23010 | PQ Event #14 |  |  | U16 | 3 | 1 | 12
23022 | PQ Event #15 |  |  | U16 | 3 | 1 | 12
23034 | PQ Event #16 |  |  | U16 | 3 | 1 | 12
23046 | PQ Event #17 |  |  | U16 | 3 | 1 | 12
23058 | PQ Event #18 |  |  | U16 | 3 | 1 | 12
23070 | PQ Event #19 |  |  | U16 | 3 | 1 | 12
23082 | PQ Event #20 |  |  | U16 | 3 | 1 | 12
23094 | PQ Event #21 |  |  | U16 | 3 | 1 | 12
23106 | PQ Event #22 |  |  | U16 | 3 | 1 | 12
23118 | PQ Event #23 |  |  | U16 | 3 | 1 | 12
23130 | PQ Event #24 |  |  | U16 | 3 | 1 | 12
23142 | PQ Event #25 |  |  | U16 | 3 | 1 | 12
23154 | PQ Event #26 |  |  | U16 | 3 | 1 | 12
23166 | PQ Event #27 |  |  | U16 | 3 | 1 | 12
23178 | PQ Event #28 |  |  | U16 | 3 | 1 | 12
23190 | PQ Event #29 |  |  | U16 | 3 | 1 | 12
23202 | PQ Event #30 |  |  | U16 | 3 | 1 | 12
23214 | PQ Event #31 |  |  | U16 | 3 | 1 | 12
23226 | PQ Event #32 |  |  | U16 | 3 | 1 | 12
23238 |  |  |  | U16 | 3 | 1 | 2
PQ Event Counter
23240 |  |  |  | U16 | 3 | 1 | 1
23241 |  |  |  | U16 | 3 | 1 | 1
23242 |  |  |  | U16 | 3 | 1 | 1
23243 | Sag Coount |  |  | U16 | 3 | 1 | 1
23244 | Swell Count |  |  | U16 | 3 | 1 | 1
23245 |  |  |  | U16 | 3 | 1 | 1
23246 |  |  |  | U16 | 3 | 1 | 1
23247 |  |  |  | U16 | 3 | 1 | 1
23248 |  |  |  | U16 | 3 | 1 | 1
23249 |  |  |  | U16 | 3 | 1 | 1
Wave Sample | [7 empty] | 32K: 67,107,786 8K: 74,518,668 첫번째 번지 접근시 wave data를 modbus map으로 load 한다
23250 | Wave Form V1 (160 sample) |  |  | S16 | 3 | 1 | 160
23410 | Wave Form V2 (160 sample) |  |  | S16 | 3 | 1 | 160
23570 | Wave Form V3 (160 sample) |  |  | S16 | 3 | 1 | 160
23730 | Wave Form V12 (160 sample) |  |  | S16 | 3 | 1 | 160
23890 | Wave Form V23 (160 sample) |  |  | S16 | 3 | 1 | 160
24050 | Wave Form V31 (160 sample) |  |  | S16 | 3 | 1 | 160
24210 | Wave Form I1 (160 sample) |  |  | S16 | 3 | 1 | 160
24370 | Wave Form I2 (160 sample) |  |  | S16 | 3 | 1 | 160
24530 | Wave Form I3 (160 sample) |  |  | S16 | 3 | 1 | 160
24690 | vscale |  |  | float | 3 | 2 | 1
24692 | iscale |  |  | float | 3 | 2 | 1
24694 |  |  |  | S16 | 3 | 1 | 6
월간리포트 생성위한 10분 평균
24700 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
24702 | U1 |  |  | float | 3 | 2 | 1
24704 | U2 |  |  | float | 3 | 2 | 1
24706 | U3 |  |  | float | 3 | 2 | 1
24708 | U THD1 |  |  | float | 3 | 2 | 1
24710 | U THD2 |  |  | float | 3 | 2 | 1
24712 | U THD3 |  |  | float | 3 | 2 | 1
24714 | Upp THD1 |  |  | float | 3 | 2 | 1
24716 | Upp THD2 |  |  | float | 3 | 2 | 1
24718 | Upp THD3 |  |  | float | 3 | 2 | 1
24720 | U Unbal Uu |  |  | float | 3 | 2 | 1
24722 | U Unbal Uo |  |  | float | 3 | 2 | 1
24724 | I1 |  |  | float | 3 | 2 | 1
24726 | I2 |  |  | float | 3 | 2 | 1
24728 | I3 |  |  | float | 3 | 2 | 1
24730 | In |  |  | float | 3 | 2 | 1
24732 | I THD1 |  |  | float | 3 | 2 | 1
24734 | I THD2 |  |  | float | 3 | 2 | 1
24736 | I THD3 |  |  | float | 3 | 2 | 1
24738 | I TDD1 |  |  | float | 3 | 2 | 1
24740 | I TDD2 |  |  | float | 3 | 2 | 1
24742 | I TDD3 |  |  | float | 3 | 2 | 1
24744 | K-factor 1 |  |  | float | 3 | 2 | 1
24746 | K-factor 2 |  |  | float | 3 | 2 | 1
24748 | K-factor 3 |  |  | float | 3 | 2 | 1
24750 | I Unbal Iu |  |  | float | 3 | 2 | 1
24752 | I Unbal Io |  |  | float | 3 | 2 | 1
24754 | kw imp |  |  | float | 3 | 2 | 1
24756 | kw exp |  |  | float | 3 | 2 | 1
24758 | kvar lag |  |  | float | 3 | 2 | 1
24760 | kvar lead |  |  | float | 3 | 2 | 1
24762 | kVA |  |  | float | 3 | 2 | 1
24764 | PF |  |  | float | 3 | 2 | 1
24766 | dPF |  |  | float | 3 | 2 | 1
24768 | temperature #1 |  |  | float | 3 | 2 | 1
24770 | temperature #2 |  |  | float | 3 | 2 | 1
24772 | temperature #3 |  |  | float | 3 | 2 | 1
24774 | temperature #4 |  |  | float | 3 | 2 | 1
24776 | temperature #5 |  |  | float | 3 | 2 | 1 | *통신이 끊어진 경우 복구를 위해 사용된다
24778 | Harmonics V1 |  |  | S16 | 3 | 1 | 24
24802 | Harmonics V2 |  |  | S16 | 3 | 1 | 24 | demand
24826 | Harmonics V3 |  |  | S16 | 3 | 1 | 24
24850 | Harmonics V12 |  |  | S16 | 3 | 1 | 24
24874 | Harmonics V23 |  |  | S16 | 3 | 1 | 24
24898 | Harmonics V31 |  |  | S16 | 3 | 1 | 24
24922 | Harmonics I1 |  |  | S16 | 3 | 1 | 24
24946 | Harmonics I2 |  |  | S16 | 3 | 1 | 24
24970 | Harmonics I3 |  |  | S16 | 3 | 1 | 24
24994 |  |  |  | U16 | 3 | 1 | 6
Energy log
25000 | Time Stamp |  |  | UTC | 3 | 2 | 1
25002 | kwh import |  |  | float | 3 | 2 | 1
25004 | kvarh lag |  |  | float | 3 | 2 | 1
25006 | kvarh lead |  |  | float | 3 | 2 | 1
25008 | kVAh |  |  | float | 3 | 2 | 1
25010 | energy log last day 01h |  |  | float | 3 | 2 | 4
25018 | energy log last day 02h |  |  | float | 3 | 2 | 4
25026 | energy log last day 03h |  |  | float | 3 | 2 | 4
25034 | energy log last day 04h |  |  | float | 3 | 2 | 4
25042 | energy log last day 05h |  |  | float | 3 | 2 | 4
25050 | energy log last day 06h |  |  | float | 3 | 2 | 4
25058 | energy log last day 07h |  |  | float | 3 | 2 | 4
25066 | energy log last day 08h |  |  | float | 3 | 2 | 4
25074 | energy log last day 09h |  |  | float | 3 | 2 | 4
25082 | energy log last day 10h |  |  | float | 3 | 2 | 4
25090 | energy log last day 11h |  |  | float | 3 | 2 | 4
25098 | energy log last day 12h |  |  | float | 3 | 2 | 4
25106 | energy log last day 13h |  |  | float | 3 | 2 | 4
25114 | energy log last day 14h |  |  | float | 3 | 2 | 4
25122 | energy log last day 15h |  |  | float | 3 | 2 | 4
25130 | energy log last day 16h |  |  | float | 3 | 2 | 4
25138 | energy log last day 17h |  |  | float | 3 | 2 | 4
25146 | energy log last day 18h |  |  | float | 3 | 2 | 4
25154 | energy log last day 19h |  |  | float | 3 | 2 | 4
25162 | energy log last day 20h |  |  | float | 3 | 2 | 4
25170 | energy log last day 21h |  |  | float | 3 | 2 | 4
25178 | energy log last day 22h |  |  | float | 3 | 2 | 4
25186 | energy log last day 23h |  |  | float | 3 | 2 | 4
25194 |  |  |  | U16 | 3 | 1 | 6
25200 | Time Stamp |  |  | UTC | 3 | 2 | 1
25202 | kwh import |  |  | float | 3 | 2 | 1
25204 | kvarh lag |  |  | float | 3 | 2 | 1
25206 | kvarh lead |  |  | float | 3 | 2 | 1
25208 | kVAh |  |  | float | 3 | 2 | 1
25210 | energy log this day 01h |  |  | float | 3 | 2 | 4
25218 | energy log this day 02h |  |  | float | 3 | 2 | 4
25226 | energy log this day 03h |  |  | float | 3 | 2 | 4
25234 | energy log this day 04h |  |  | float | 3 | 2 | 4
25242 | energy log this day 05h |  |  | float | 3 | 2 | 4
25250 | energy log this day 06h |  |  | float | 3 | 2 | 4
25258 | energy log this day 07h |  |  | float | 3 | 2 | 4
25266 | energy log this day 08h |  |  | float | 3 | 2 | 4
25274 | energy log this day 09h |  |  | float | 3 | 2 | 4
25282 | energy log this day 10h |  |  | float | 3 | 2 | 4
25290 | energy log this day 11h |  |  | float | 3 | 2 | 4
25298 | energy log this day 12h |  |  | float | 3 | 2 | 4
25306 | energy log this day 13h |  |  | float | 3 | 2 | 4
25314 | energy log this day 14h |  |  | float | 3 | 2 | 4 | 전일 디멘트 로그
25322 | energy log this day 15h |  |  | float | 3 | 2 | 4
25330 | energy log this day 16h |  |  | float | 3 | 2 | 4
25338 | energy log this day 17h |  |  | float | 3 | 2 | 4
25346 | energy log this day 18h |  |  | float | 3 | 2 | 4
25354 | energy log this day 19h |  |  | float | 3 | 2 | 4
25362 | energy log this day 20h |  |  | float | 3 | 2 | 4
25370 | energy log this day 21h |  |  | float | 3 | 2 | 4
25378 | energy log this day 22h |  |  | float | 3 | 2 | 4
25386 | energy log this day 23h |  |  | float | 3 | 2 | 4
25394 |  |  |  | U16 | 3 | 1 | 6
demand log last day
25400 | Time Stamp |  |  | U32 | 3 | 2 | 1
25402 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
25594 |  |  |  | U16 | 3 | 1 | 6
ITIC
25600 | fr |  |  | U16 | 3 | 1 | 1
25601 | re |  |  | U16 | 3 | 1 | 1
25602 | count |  |  | U16 | 3 | 1 | 1
25603 | SEQ |  |  | U16 | 3 | 1 | 1
25604 | Log #1 | start ts |  | UTC | 3 | 2 | 1
25606 |  | start ts(ms) |  | U16 | 3 | 1 | 1
25607 |  | duration |  | U16 | 3 | 1 | 1
25608 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
25609 |  | mask |  | U16 | 3 | 1 | 1
25610 |  | Level 1 |  | float | 3 | 2 | 1
25612 |  | Level 2 |  | float | 3 | 2 | 1
25614 |  | Level 3 |  | float | 3 | 2 | 1
25616 |  | Normal |  | float | 3 | 2 | 1
25618 | Log #2 |  |  | U16 | 3 | 1 | 14
25632 | Log #3 |  |  | U16 | 3 | 1 | 14
25646 | Log #4 |  |  | U16 | 3 | 1 | 14
25660 | Log #5 |  |  | U16 | 3 | 1 | 14
25674 | Log #6 |  |  | U16 | 3 | 1 | 14
25688 | Log #7 |  |  | U16 | 3 | 1 | 14
25702 | Log #8 |  |  | U16 | 3 | 1 | 14
25716 | Log #9 |  |  | U16 | 3 | 1 | 14
25730 | Log #10 |  |  | U16 | 3 | 1 | 14
25744 | Log #11 |  |  | U16 | 3 | 1 | 14
25758 | Log #12 |  |  | U16 | 3 | 1 | 14
25772 | Log #13 |  |  | U16 | 3 | 1 | 14
25786 | Log #14 |  |  | U16 | 3 | 1 | 14
25800 | Log #15 |  |  | U16 | 3 | 1 | 14
25814 | Log #16 |  |  | U16 | 3 | 1 | 14
25828 | Log #17 |  |  | U16 | 3 | 1 | 14
25842 | Log #18 |  |  | U16 | 3 | 1 | 14
25856 | Log #19 |  |  | U16 | 3 | 1 | 14
25870 | Log #20 |  |  | U16 | 3 | 1 | 14
25884 | Log #21 |  |  | U16 | 3 | 1 | 14
25898 | Log #22 |  |  | U16 | 3 | 1 | 14
25912 | Log #23 |  |  | U16 | 3 | 1 | 14
25926 | Log #24 |  |  | U16 | 3 | 1 | 14
25940 | Log #25 |  |  | U16 | 3 | 1 | 14
25954 | Log #26 |  |  | U16 | 3 | 1 | 14
25968 | Log #27 |  |  | U16 | 3 | 1 | 14
25982 | Log #28 |  |  | U16 | 3 | 1 | 14
25996 | Log #29 |  |  | U16 | 3 | 1 | 14
26010 | Log #30 |  |  | U16 | 3 | 1 | 14
26024 | Log #31 |  |  | U16 | 3 | 1 | 14
26038 | Log #32 |  |  | U16 | 3 | 1 | 14
26052 |  |  |  | U16 | 3 | 1 | 8
ITIC(Configurator)
26060 | fr |  |  | U16 | 3 | 1 | 1
26061 | re |  |  | U16 | 3 | 1 | 1
26062 | count |  |  | U16 | 3 | 1 | 1
26063 | reserved |  |  | U16 | 3 | 1 | 1
26064 | Log #1 | start ts |  | UTC | 3 | 2 | 1
26066 |  | start ts(ms) |  | U16 | 3 | 1 | 1
26067 |  | duration |  | U16 | 3 | 1 | 1
26068 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
26069 |  | mask |  | U16 | 3 | 1 | 1
26070 |  | Level 1 |  | float | 3 | 2 | 1
26072 |  | Level 2 |  | float | 3 | 2 | 1
26074 |  | Level 3 |  | float | 3 | 2 | 1
26076 |  | Normal |  | float | 3 | 2 | 1
26078 | Log #2 |  |  | U16 | 3 | 1 | 14
26092 | Log #3 |  |  | U16 | 3 | 1 | 14
26106 | Log #4 |  |  | U16 | 3 | 1 | 14
26120 | Log #5 |  |  | U16 | 3 | 1 | 14
26134 | Log #6 |  |  | U16 | 3 | 1 | 14
26148 | Log #7 |  |  | U16 | 3 | 1 | 14
26162 | Log #8 |  |  | U16 | 3 | 1 | 14
26176 | Log #9 |  |  | U16 | 3 | 1 | 14
26190 | Log #10 |  |  | U16 | 3 | 1 | 14
26204 | Log #11 |  |  | U16 | 3 | 1 | 14
26218 | Log #12 |  |  | U16 | 3 | 1 | 14
26232 | Log #13 |  |  | U16 | 3 | 1 | 14
26246 | Log #14 |  |  | U16 | 3 | 1 | 14
26260 | Log #15 |  |  | U16 | 3 | 1 | 14
26274 | Log #16 |  |  | U16 | 3 | 1 | 14
26288 | Log #17 |  |  | U16 | 3 | 1 | 14
26302 | Log #18 |  |  | U16 | 3 | 1 | 14
26316 | Log #19 |  |  | U16 | 3 | 1 | 14
26330 | Log #20 |  |  | U16 | 3 | 1 | 14
26344 | Log #21 |  |  | U16 | 3 | 1 | 14
26358 | Log #22 |  |  | U16 | 3 | 1 | 14
26372 | Log #23 |  |  | U16 | 3 | 1 | 14
26386 | Log #24 |  |  | U16 | 3 | 1 | 14
26400 | Log #25 |  |  | U16 | 3 | 1 | 14
26414 | Log #26 |  |  | U16 | 3 | 1 | 14
26428 | Log #27 |  |  | U16 | 3 | 1 | 14
26442 | Log #28 |  |  | U16 | 3 | 1 | 14
26456 | Log #29 |  |  | U16 | 3 | 1 | 14
26470 | Log #30 |  |  | U16 | 3 | 1 | 14
26484 | Log #31 |  |  | U16 | 3 | 1 | 14
26498 | Log #32 |  |  | U16 | 3 | 1 | 14
26512 |  |  |  | U16 | 3 | 1 | 8
Setting 영역 시작
PQ Event
26520 | OC Level | 정격의 2배 |  | U16 | 3,16 | 1 | 1
26521 | OC Cycle | unused |  | U16 | 3,16 | 1 | 1
26522 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
26523 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
26524 |  |  |  | U16 | 3,16 | 1 | 2
26526 | Sag Level(%), 90% | < 90% |  | U16 | 3,16 | 1 | 1
26527 | Sag Cycle | unused |  | U16 | 3,16 | 1 | 1
26528 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
26529 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
26530 |  |  |  | U16 | 3,16 | 1 | 2
26532 | Swell Level(%), 110~200~ | > 110% |  | U16 | 3,16 | 1 | 1
26533 | Swell Cycle | unused |  | U16 | 3,16 | 1 | 1
26534 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
26535 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
26536 |  |  |  | U16 | 3,16 | 1 | 2
26538 | Interruption Level, 5% | < 5% |  | U16 | 3,16 | 1 | 1
26539 | Interruption Time, 60s | unused |  | U16 | 3,16 | 1 | 1
26540 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
26541 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
26542 |  |  |  | U16 | 3,16 | 1 | 2
Transient Trigger
26544 | Transient Voltage, HoldOff Time, 20ms | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
26545 | Transient Voltage, Absolute Peak Level, 200% | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
26546 | Transient Voltage, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
26547 | Transient Voltage, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
26548 | Transient Current, HoldOff Time | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
26549 | Transient Current, Absolute Peak Level | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
26550 | Transient Current, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
26551 | Transient Current, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
26552 |  |  |  | U16 | 3,16 | 1 | 12
Recorder
Waveform
26564 | Recorder resolution(32k, 8k) |  |  | U16 | 3,16 | 1 | 1
26565 | Recorded paramater (U or I) |  |  | U16 | 3,16 | 1 | 1
26566 | pre trigger time(0.1s) |  |  | U16 | 3,16 | 1 | 1
26567 | post trigger time(1s) |  |  | U16 | 3,16 | 1 | 1
Disturbance
26568 | Recorder resolution (Half Cycle) |  |  | U16 | 3,16 | 1 | 1
26569 | Recorded parametrs(U or I) |  |  | U16 | 3,16 | 1 | 1
26570 | pre trigger time(100 sample) |  |  | U16 | 3,16 | 1 | 1
26571 | post trigger time(900 sample) |  |  | U16 | 3,16 | 1 | 1
26572 |  |  |  | U16 | 3,16 | 1 | 12
Trend Recorder
26584 | Trend Group #1 Active |  |  | U16 | 3,16 | 1 | 1
26585 | Trend Group #1 Storage Interval |  |  | U16 | 3,16 | 1 | 1
26586 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
26587 | Trend Group #1, Channel #1 |  |  | U16 | 3,16 | 1 | 1
26588 | Trend Group #1, Channel #2 |  |  | U16 | 3,16 | 1 | 1
26589 | Trend Group #1, Channel #3 |  |  | U16 | 3,16 | 1 | 1
26590 | Trend Group #1, Channel #4 |  |  | U16 | 3,16 | 1 | 1
26591 | Trend Group #1, Channel #5 |  |  | U16 | 3,16 | 1 | 1
26592 | Trend Group #1, Channel #6 |  |  | U16 | 3,16 | 1 | 1
26593 | Trend Group #1, Channel #7 |  |  | U16 | 3,16 | 1 | 1
26594 | Trend Group #1, Channel #8 |  |  | U16 | 3,16 | 1 | 1
26595 | Trend Group #1, Channel #9 |  |  | U16 | 3,16 | 1 | 1
26596 | Trend Group #1, Channel #10 |  |  | U16 | 3,16 | 1 | 1
26597 | Trend Group #1, Channel #11 |  |  | U16 | 3,16 | 1 | 1
26598 | Trend Group #1, Channel #12 |  |  | U16 | 3,16 | 1 | 1
26599 | Trend Group #1, Channel #13 |  |  | U16 | 3,16 | 1 | 1
26600 | Trend Group #1, Channel #14 |  |  | U16 | 3,16 | 1 | 1
26601 | Trend Group #1, Channel #15 |  |  | U16 | 3,16 | 1 | 1
26602 | Trend Group #1, Channel #16 |  |  | U16 | 3,16 | 1 | 1
26603 | Trend Group #2 Active |  |  | U16 | 3,16 | 1 | 1
26604 | Trend Group #2 Storage Interval |  |  | U16 | 3,16 | 1 | 1
26605 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
26606 | Trend Group #2, Channel #1 |  |  | U16 | 3,16 | 1 | 1
26607 | Trend Group #2, Channel #2 |  |  | U16 | 3,16 | 1 | 1
26608 | Trend Group #2, Channel #3 |  |  | U16 | 3,16 | 1 | 1
26609 | Trend Group #2, Channel #4 |  |  | U16 | 3,16 | 1 | 1
26610 | Trend Group #2, Channel #5 |  |  | U16 | 3,16 | 1 | 1
26611 | Trend Group #2, Channel #6 |  |  | U16 | 3,16 | 1 | 1
26612 | Trend Group #2, Channel #7 |  |  | U16 | 3,16 | 1 | 1
26613 | Trend Group #2, Channel #8 |  |  | U16 | 3,16 | 1 | 1
26614 | Trend Group #2, Channel #9 |  |  | U16 | 3,16 | 1 | 1
26615 | Trend Group #2, Channel #10 |  |  | U16 | 3,16 | 1 | 1
26616 | Trend Group #2, Channel #11 |  |  | U16 | 3,16 | 1 | 1
26617 | Trend Group #2, Channel #12 |  |  | U16 | 3,16 | 1 | 1
26618 | Trend Group #2, Channel #13 |  |  | U16 | 3,16 | 1 | 1
26619 | Trend Group #2, Channel #14 |  |  | U16 | 3,16 | 1 | 1
26620 | Trend Group #2, Channel #15 |  |  | U16 | 3,16 | 1 | 1
26621 | Trend Group #2, Channel #16 |  |  | U16 | 3,16 | 1 | 1
26622 | Trend Group #3 Active |  |  | U16 | 3,16 | 1 | 1
26623 | Trend Group #3 Storage Interval |  |  | U16 | 3,16 | 1 | 1
26624 |  |  |  | U16 | 3,16 | 1 | 1
26625 | Trend Group #3, Channel #1 |  |  | U16 | 3,16 | 1 | 1
26626 | Trend Group #3, Channel #2 |  |  | U16 | 3,16 | 1 | 1
26627 | Trend Group #3, Channel #3 |  |  | U16 | 3,16 | 1 | 1
26628 | Trend Group #3, Channel #4 |  |  | U16 | 3,16 | 1 | 1
26629 | Trend Group #3, Channel #5 |  |  | U16 | 3,16 | 1 | 1
26630 | Trend Group #3, Channel #6 |  |  | U16 | 3,16 | 1 | 1
26631 | Trend Group #3, Channel #7 |  |  | U16 | 3,16 | 1 | 1
26632 | Trend Group #3, Channel #8 |  |  | U16 | 3,16 | 1 | 1
26633 | Trend Group #3, Channel #9 |  |  | U16 | 3,16 | 1 | 1
26634 | Trend Group #3, Channel #10 |  |  | U16 | 3,16 | 1 | 1
26635 | Trend Group #3, Channel #11 |  |  | U16 | 3,16 | 1 | 1
26636 | Trend Group #3, Channel #12 |  |  | U16 | 3,16 | 1 | 1
26637 | Trend Group #3, Channel #13 |  |  | U16 | 3,16 | 1 | 1
26638 | Trend Group #3, Channel #14 |  |  | U16 | 3,16 | 1 | 1
26639 | Trend Group #3, Channel #15 |  |  | U16 | 3,16 | 1 | 1
26640 | Trend Group #3, Channel #16 |  |  | U16 | 3,16 | 1 | 1
26641 | Trend Group #4 Active |  |  | U16 | 3,16 | 1 | 1
26642 | Trend Group #4 Storage Interval |  |  | U16 | 3,16 | 1 | 1
26643 |  |  |  | U16 | 3,16 | 1 | 1
26644 | Trend Group #4, Channel #1 |  |  | U16 | 3,16 | 1 | 1
26645 | Trend Group #4, Channel #2 |  |  | U16 | 3,16 | 1 | 1
26646 | Trend Group #4, Channel #3 |  |  | U16 | 3,16 | 1 | 1
26647 | Trend Group #4, Channel #4 |  |  | U16 | 3,16 | 1 | 1
26648 | Trend Group #4, Channel #5 |  |  | U16 | 3,16 | 1 | 1
26649 | Trend Group #4, Channel #6 |  |  | U16 | 3,16 | 1 | 1
26650 | Trend Group #4, Channel #7 |  |  | U16 | 3,16 | 1 | 1
26651 | Trend Group #4, Channel #8 |  |  | U16 | 3,16 | 1 | 1
26652 | Trend Group #4, Channel #9 |  |  | U16 | 3,16 | 1 | 1
26653 | Trend Group #4, Channel #10 |  |  | U16 | 3,16 | 1 | 1
26654 | Trend Group #4, Channel #11 |  |  | U16 | 3,16 | 1 | 1
26655 | Trend Group #4, Channel #12 |  |  | U16 | 3,16 | 1 | 1
26656 | Trend Group #4, Channel #13 |  |  | U16 | 3,16 | 1 | 1
26657 | Trend Group #4, Channel #14 |  |  | U16 | 3,16 | 1 | 1
26658 | Trend Group #4, Channel #15 |  |  | U16 | 3,16 | 1 | 1
26659 | Trend Group #4, Channel #16 |  |  | U16 | 3,16 | 1 | 1
26660 |  |  |  | U16 | 3,16 | 1 | 4
Power Quality Report
26664 | Active |  |  | U16 | 3,16 | 1 | 1
26665 | Start Day |  |  | U16 | 3,16 | 1 | 1
26666 |  |  |  | U16 |  | 1 | 8
Alarm Definition
26674 | compare Time Delay(1s) |  |  | U16 | 3,16 | 1 | 1
26675 |  |  |  | U16 |  | 1 | 1
26676 |  |  |  | U16 |  | 1 | 1
26677 |  |  |  | U16 |  | 1 | 1
Alarm Settings
26678 | Alarm Info #1 Channel(0:disabled, >0: enabled) |  |  | U16 | 3,16 | 1 | 1
26679 | Alarm Cond (0: < , 1:>) |  |  | U16 | 3,16 | 1 | 1
26680 | Hysteresis (% of Nominal) |  |  | U16 | 3,16 | 1 | 1
26681 | Alarm Action (None, Relay or Beep) |  |  | U16 | 3,16 | 1 | 1
26682 | Alarm Level |  |  | float | 3,16 | 2 | 1
26684 | Alarm Settings #2 |  |  | U16 | 3,16 | 1 | 6
26690 | Alarm Settings #3 |  |  | U16 | 3,16 | 1 | 6
26696 | Alarm Settings #4 |  |  | U16 | 3,16 | 1 | 6
26702 | Alarm Settings #5 |  |  | U16 | 3,16 | 1 | 6
26708 | Alarm Settings #6 |  |  | U16 | 3,16 | 1 | 6
26714 | Alarm Settings #7 |  |  | U16 | 3,16 | 1 | 6
26720 | Alarm Settings #8 |  |  | U16 | 3,16 | 1 | 6
26726 | Alarm Settings #9 |  |  | U16 | 3,16 | 1 | 6
26732 | Alarm Settings #10 |  |  | U16 | 3,16 | 1 | 6
26738 | Alarm Settings #11 |  |  | U16 | 3,16 | 1 | 6
26744 | Alarm Settings #12 |  |  | U16 | 3,16 | 1 | 6
26750 | Alarm Settings #13 |  |  | U16 | 3,16 | 1 | 6
26756 | Alarm Settings #14 |  |  | U16 | 3,16 | 1 | 6
26762 | Alarm Settings #15 |  |  | U16 | 3,16 | 1 | 6
26768 | Alarm Settings #16 |  |  | U16 | 3,16 | 1 | 6
26774 | Alarm Settings #17 |  |  | U16 | 3,16 | 1 | 6
26780 | Alarm Settings #18 |  |  | U16 | 3,16 | 1 | 6
26786 | Alarm Settings #19 |  |  | U16 | 3,16 | 1 | 6
26792 | Alarm Settings #20 |  |  | U16 | 3,16 | 1 | 6
26798 | Alarm Settings #21 |  |  | U16 | 3,16 | 1 | 6
26804 | Alarm Settings #22 |  |  | U16 | 3,16 | 1 | 6
26810 | Alarm Settings #23 |  |  | U16 | 3,16 | 1 | 6
26816 | Alarm Settings #24 |  |  | U16 | 3,16 | 1 | 6
26822 | Alarm Settings #25 |  |  | U16 | 3,16 | 1 | 6
26828 | Alarm Settings #26 |  |  | U16 | 3,16 | 1 | 6
26834 | Alarm Settings #27 |  |  | U16 | 3,16 | 1 | 6
26840 | Alarm Settings #28 |  |  | U16 | 3,16 | 1 | 6
26846 | Alarm Settings #29 |  |  | U16 | 3,16 | 1 | 6
26852 | Alarm Settings #30 |  |  | U16 | 3,16 | 1 | 6
26858 | Alarm Settings #31 |  |  | U16 | 3,16 | 1 | 6
26864 | Alarm Settings #32 |  |  | U16 | 3,16 | 1 | 6

## Alarm Channel
Trend/Alarm Channel
1 | Temp
2 | Freq
3 | U1
4 | U2
5 | U3
6 | U~
7 | U12
8 | U23
9 | U31
10 | Upp~
11 | Voltage Unbalace, Uo
12 | Voltage Unbalace, Uu
13 | I1
14 | I2
15 | I3
16 | I~
17 | Itotal
18 | In
19 | P1
20 | P2
21 | P3
22 | Ptotal
23 | Q1
24 | Q2
25 | Q3
26 | Qtot
27 | D1
28 | D2
29 | D3
30 | D
31 | S1
32 | S2
33 | S3
34 | Stot
35 | PF1
36 | PF2
37 | PF3
38 | PFtot
39 | THD U1
40 | THD U2
41 | THD U3
42 | THD U12
43 | THD U23
44 | THD U31
45 | THD I1
46 | THD I2
47 | THD I3
48 | Dynamic Demand P+
49 | Dynamic Demand P-
50 | Dynamic Demand Q+
51 | Dynamic Demand Q-
52 | Dynamic Demand S
53 | Dynamic Demand I1
54 | Dynamic Demand I2
55 | Dynamic Demand I3
56 | Max. Demand P+
57 | Max. Demand P=-
58 | Max. Demand Q+
59 | Max. Demand Q-
60 | Max. Demand S
61 | Max. Demand I1
62 | Max. Demand I2
63 | Max. Demand I3
64 | Under Deviation U1
65 | Under Deviation U2
66 | Under Deviation U3
67 | Over Drviation U1
68 | Over Drviation U2
69 | Over Drviation U3
70 | CF U1
71 | CF U2
72 | CF U3
73 | CF U12
74 | CF U23
75 | CF U31
76 | CF I1
77 | CF I2
78 | CF I3
79 | KF I1
80 | KF I2
81 | KF I3
82 | PSt 1
83 | PSt 2
84 | PSt 3
85 | Plt 1
86 | Plt 2
87 | Plt 3
88 | Sig. Volt 1
89 | Sig. Volt 2
90 | Sig. Volt 3