## ToDo&Log
date | description | addr
2024-12-18 | 1st draft
2026-05-13 | 3ch redefine
2026-06-18 | ENERGY PHASE L1,2,3 ADD | 240~479

## #1,2,3 Simple
address | Group | name | Decription | 1P | 3P | Unit | Function code | TYPE | 1P | 3P | Word Count | Item Count
Metering
50000 | Common | Time Stamp |  |  |  |  | 3,4 | U32 |  |  | 2 | 1
50002 |  | Heatbit |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50003 |  | HW Model |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50004 |  | HW Version |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50005 |  | FW Version |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50006 |  | FW_BUILD_YEAR |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50007 |  | FW_BUILD_MON |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50008 |  | FW_BUILD_DAY |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50009 |  | Serial Num |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50010 |  | Status |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50011 |  | reserved |  |  |  |  | 3,4 | U16 |  |  | 1 | 1
50012 |  | Internal Temp |  |  |  |  | 3,4 | float |  |  | 2 | 1
50014 |  | reserved |  |  |  |  | 3,4 | U32 |  |  | 2 | 3
50020 | #1 | CB Type |  | ● | ● |  | 3,4 | U16 |  |  | 1 | 1
50021 |  | CB Status |  | ● | ● |  | 3,4 | U16 |  |  | 1 | 1
50022 |  | reserved |  | ● | ● |  | 3,4 | U32 |  |  | 2 | 1
50024 |  | Frequency |  | ● | ● | Hz | 3,4 | float |  |  | 2 | 1
50026 |  | U1 | 상전압 1 | ● | ● | V | 3,4 | float |  |  | 2 | 1
50028 |  | U2 | 상전압 2 |  | ● |  | 3,4 | float |  |  | 2 | 1
50030 |  | U3 | 상전압 3 |  | ● |  | 3,4 | float |  |  | 2 | 1
50032 |  | U12 |  |  | ● |  | 3,4 | float |  |  | 2 | 1
50034 |  | U23 |  |  | ● |  | 3,4 | float |  |  | 2 | 1
50036 |  | U31 |  |  | ● |  | 3,4 | float |  |  | 2 | 1
50038 |  | I1 | 상전류 1 | ● | ● | A | 3,4 | float |  |  | 2 | 1
50040 |  | I2 | 상전류 2 |  | ● |  | 3,4 | float |  |  | 2 | 1
50042 |  | I3 | 상전류 3 |  | ● |  | 3,4 | float |  |  | 2 | 1
50044 |  | In | 누설전류 |  | ● |  | 3,4 | float |  |  | 2 | 1
50046 |  | P1 |  | ● | ● | W | 3,4 | float |  |  | 2 | 1
50048 |  | P2 |  |  | ● |  | 3,4 | float |  |  | 2 | 1
50050 |  | P3 |  |  | ● |  | 3,4 | float |  |  | 2 | 1
50052 |  | P total |  | ● | ● |  | 3,4 | float |  |  | 2 | 1
50054 |  | Q total |  | ● | ● | Var | 3,4 | float |  |  | 2 | 1
50056 |  | S total |  | ● | ● | VA | 3,4 | float |  |  | 2 | 1
50058 |  | PF total |  | ● | ● | % | 3,4 | float |  |  | 2 | 1
50060 |  | kWh_imp |  | ● | ● | kWh | 3,4 | U32 |  |  | 2 | 1
50062 |  | kWh_imp_this_month |  | ● | ● | kWh | 3,4 | U32 |  |  | 2 | 1
50064 |  | kWh_imp_last_month |  | ● | ● | kWh | 3,4 | U32 |  |  | 2 | 1
50066 |  | kVARh_imp |  | ● | ● | kVarh | 3,4 | U32 |  |  | 2 | 1
50068 |  | kVAh |  | ● | ● | kVAh | 3,4 | U32 |  |  | 2 | 1
50070 |  | Volt. Unbalance |  | ● | ● | % | 3,4 | float |  |  | 2 | 1
50072 |  | Current Unbalance |  | ● | ● | % | 3,4 | float |  |  | 2 | 1
50074 |  | THD V1 | 고조파함유율 상전압 1 | ● | ● | % | 3,4 | float |  |  | 2 | 1
50076 |  | THD V2 | 고조파함유율 상전압 2 |  | ● | % | 3,4 | float |  |  | 2 | 1
50078 |  | THD V3 | 고조파함유율 상전압 3 |  | ● | % | 3,4 | float |  |  | 2 | 1
50080 |  | THD I1 | 고조파함유율 상전류 1 | ● | ● | % | 3,4 | float |  |  | 2 | 1
50082 |  | THD I2 | 고조파함유율 상전류 2 |  | ● | % | 3,4 | float |  |  | 2 | 1
50084 |  | THD I3 | 고조파함유율 상전류 3 |  | ● | % | 3,4 | float |  |  | 2 | 1
50086 |  | TDD I1 | 디맨드왜형율 상전류 1 | ● | ● | % | 3,4 | float |  |  | 2 | 1
50088 |  | TDD I2 | 디맨드왜형율 상전류 2 |  | ● | % | 3,4 | float |  |  | 2 | 1
50090 |  | TDD I3 | 디맨드왜형율 상전류 3 |  | ● | % | 3,4 | float |  |  | 2 | 1
50092 |  | reserved |  | ● | ● |  | 3,4 | float |  |  | 2 | 4
50100 | #2 |  |  | ● | ● |  | 3,4 | float |  |  | 1 | 80
50180 | #3 |  |  | ● | ● |  | 3,4 | float |  |  | 1 | 80
50260 | #4 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
50340 | #5 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
50420 | #6 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
50500 | #7 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
50580 | #8 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
50660 | #9 |  |  | ● |  |  | 3,4 | float |  |  | 1 | 80
Harmonics by order
50740 | #1 | Harmonics V1 | 1~41th | ● | ● |  | 3,4 | S16 |  |  | 1 | 41
50781 |  | Harmonics V2 |  |  | ● |  | 3,4 | S16 |  |  | 1 | 41
50822 |  | Harmonics V3 |  |  | ● |  | 3,4 | S16 |  |  | 1 | 41
50863 |  | Harmonics I1 |  | ● | ● |  | 3,4 | S16 |  |  | 1 | 41
50904 |  | Harmonics I2 |  |  | ● |  | 3,4 | S16 |  |  | 1 | 41
50945 |  | Harmonics I3 |  |  | ● |  | 3,4 | S16 |  |  | 1 | 41
50986 | #2 |  |  | ● | ● | [5 empty] | 1 | 246
51232 | #3 |  |  | ● | ● | [5 empty] | 1 | 246
51478 | #4 |  |  | ● | [6 empty] | 1 | 246
51724 | #5 |  |  | ● | [6 empty] | 1 | 246
51970 | #6 |  |  | ● | [6 empty] | 1 | 246
52216 | #7 |  |  | ● | [6 empty] | 1 | 246
52462 | #8 |  |  | ● | [6 empty] | 1 | 246
52708 | #9 |  |  | ● | [6 empty] | 1 | 246

## common
address | name | 설명 | Unit | TYPE | FC | Word Count | Item Count
IOM Data
7050 | DI status #0 |  |  | U16 | 3 | 1 | 1
7051 | DI status #1 |  |  | U16 | 3 | 1 | 1
7052 | DI status #2 |  |  | U16 | 3 | 1 | 1
7053 | DI status #3 |  |  | U16 | 3 | 1 | 1
7054 | DI Pulse Data #0 |  |  | U32 | 3 | 2 | 1
7056 | DI Pulse Data #1 |  |  | U32 | 3 | 2 | 1
7058 | DI Pulse Data #2 |  |  | U32 | 3 | 2 | 1
7060 | DI Pulse Data #3 |  |  | U32 | 3 | 2 | 1
7062 | TEMP #0 |  |  | float | 3 | 2 | 1
7064 | TEMP #1 |  |  | float | 3 | 2 | 1
7066 | TEMP #2 |  |  | float | 3 | 2 | 1
7068 | TEMP #3 |  |  | float | 3 | 2 | 1
METER INFO
7070 | serial# |  |  | U16 | 3 | 1 | 6
7076 | MAC MSB |  |  | U16 | 3 | 1 | 2
7078 | mac address |  |  | U16 | 3 | 1 | 4
7082 | IP ADDR |  |  | U16 | 3 | 1 | 4
7086 | HW Model |  |  | U16 | 3 | 1 | 1
7087 | HW version |  |  | U16 | 3 | 1 | 1
7088 | FW version |  |  | U16 | 3 | 1 | 1
7089 | FW_BUILD_YEAR |  |  | U16 | 3 | 1 | 1
7090 | FW_BUILD_MON |  |  | U16 | 3 | 1 | 1
7091 | FW_BUILD_DAY |  |  | U16 | 3 | 1 | 1
7092 | HEART BIT |  |  | U16 | 3 | 1 | 1
7093 | MODBUS RX COUNT |  |  | U16 | 3 | 1 | 1
7094 | ALARM STS |  |  | U16 | 3 | 1 | 1
7095 | EVENT STS |  |  | U16 | 3 | 1 | 1
7096 | RSTP STS[0~1] |  |  | U16 | 3 | 1 | 2
7098 | SNTP STS |  |  | U16 | 3 | 1 | 1
7099 | DEV STS |  |  | U16 | 3 | 1 | 1
7100 | NET STS |  |  | U16 | 3 | 1 | 1
7101 | TOT STS |  |  | U16 | 3 | 1 | 1
7102 | reserved |  |  | U16 | 3 | 1 | 8
Communication Settings
7110 | device Id |  |  | U16 | 3,16 | 1 | 1
7111 | Modbus TCP Port |  |  | U16 | 3,16 | 1 | 1
7112 | SNTP Mode | 0 : not use, 1 : use |  | U16 | 3,16 | 1 | 1
7113 | SNTP Interval |  | min | U16 | 3,16 | 1 | 1
7114 | Eth#0 IP |  |  | U16 | 3,16 | 1 | 4
7118 | Eth#0 SUBNET |  |  | U16 | 3,16 | 1 | 4
7122 | Eth#0 GATEWAY |  |  | U16 | 3,16 | 1 | 4
7126 | Eth#0 DNS |  |  | U16 | 3,16 | 1 | 4
7130 | SNTP IP |  |  | U16 | 3,16 | 1 | 4
7134 | Host Name |  |  | U16 | 3,16 | 1 | 16
7150 | DAQ server ip |  |  | U16 | 3,16 | 1 | 4
7154 | DHCP enabled |  |  | U16 | 3,16 | 1 | 1
7155 | DAQ sampling rate (0: 2k, 1: 4k, 2: 8k, 3: 16k, 4: 32k) |  |  | U16 | 3,16 | 1 | 1
7156 | DAQ sampling buffer length (0: 2k, 1: 4k, 2: 8k, 3: 16k, 4: 32k, 5: 64) |  |  | U16 | 3,16 | 1 | 1
7157 | DAQ interval (minute) |  |  | U16 | 3,16 | 1 | 1
7158 | DAQ format |  |  | U16 | 3,16 | 1 | 1
7159 | DAQ device id |  |  | U16 | 3,16 | 1 | 1
7160 | DAQ bitspersample (0: 16bit, 1: 32bit) |  |  | U16 | 3,16 | 1 | 1
7161 | reserved |  |  | U16 | 3,16 | 1 | 9
PT #1~9
7170 | Frequency |  |  | U16 | 3,16 | 1 | 1
7171 | feeder count |  |  | U16 | 3,16 | 1 | 1
7172 | #1 wiring mode | 0: not used 1 : 3p4w 2 : 3p3w(2CT), 3 : 3p3w(3CT) 4: 1p2w(L1), 5 : 1p2w(L2), 6 : 1p2w(L3) 7: 1p3w 8 : SIMULATION |  | U16 | 3,16 | 1 | 1
7173 | #1 reserved |  |  | U16 | 3,16 | 1 | 1
7174 | #1 V nominal |  |  | U32 | 3,16 | 2 | 1
7176 | #1 PT1 |  |  | U32 | 3,16 | 2 | 1
7178 | #1 PT2 |  |  | U16 | 3,16 | 1 | 1
7179 | #1 reserved |  |  | U16 | 3,16 | 1 | 1
7180 | #2 PT |  |  | U16 | 3,16 | 1 | 8
7188 | #3 PT |  |  | U16 | 3,16 | 1 | 8
7196 | #4 PT |  |  | U16 | 3,16 | 1 | 8
7204 | #5 PT |  |  | U16 | 3,16 | 1 | 8
7212 | #6 PT |  |  | U16 | 3,16 | 1 | 8
7220 | #7 PT |  |  | U16 | 3,16 | 1 | 8
7228 | #8 PT |  |  | U16 | 3,16 | 1 | 8
7236 | #9 PT |  |  | U16 | 3,16 | 1 | 8
CT #1~9
7244 | #1 I Nominal |  |  | U16 | 3,16 | 1 | 1
7245 | #1 CT1 |  |  | U16 | 3,16 | 1 | 1
7246 | #1 CT2 | 0: 5A, 1: 100mA/333mV, 2: Rogowski |  | U16 | 3,16 | 1 | 1
7247 | #1 turns |  |  | U16 | 3,16 | 1 | 1
7248 | #1 Starting Current | (1.0 : 0.002*In, 0.5: 0.001*In) 0 ~ 10000 (단위 : mA) |  | U16 | 3,16 | 1 | 1
7249 | #1 CT1 direction | 0: positive, 1: negative |  | U16 | 3,16 | 1 | 1
7250 | #1 CT2 direction |  |  | U16 | 3,16 | 1 | 1
7251 | #1 CT3 direction |  |  | U16 | 3,16 | 1 | 1
7252 | #1 Rogowski CT Model |  |  | U16 | 3,16 | 1 | 1
7253 | #1 phase offset 1 | * phase resolution 60Hz: 0.0211, 50Hz: 0.0176 * range: +63 ~ -383 1.329 ~ -8.079 1.107 ~ -6.732 |  | U16 | 3,16 | 1 | 1
7254 | #1 phase offset 2 |  |  | U16 | 3,16 | 1 | 1
7255 | #1 phase offset 3 |  |  | U16 | 3,16 | 1 | 1
7256 | #1 ZCT Type | 1: 200mV:100mV 2: 200mV:1.5mA 3: 200mV:0.1mA |  | U16 | 3,16 | 1 | 1
7257 | #1 ZCT Scale |  |  | U16 | 3,16 | 1 | 1
7258 | #1 reserved |  |  | U16 | 3,16 | 1 | 2
7260 | #2 CT |  |  | U16 | 3,16 | 1 | 16
7276 | #3 CT |  |  | U16 | 3,16 | 1 | 16
7292 | #4 CT |  |  | U16 | 3,16 | 1 | 16
7308 | #5 CT |  |  | U16 | 3,16 | 1 | 16
7324 | #6 CT |  |  | U16 | 3,16 | 1 | 16
7340 | #7 CT |  |  | U16 | 3,16 | 1 | 16
7356 | #8 CT |  |  | U16 | 3,16 | 1 | 16
7372 | #9 CT |  |  | U16 | 3,16 | 1 | 16
ETC
7388 | VA type | 0: RMS(S=VA) 1: vector(S=sqrt(P*P+Q*Q) |  | U16 | 3,16 | 1 | 1
7389 | PF sign | 0: IEC, 1: IEEE |  | U16 | 3,16 | 1 | 1
7390 | demand interval |  |  | U16 | 3,16 | 1 | 1
7391 | Max. Demand for current TDD(A) - unused |  |  | U16 | 3,16 | 1 | 1
7392 | Target Demand (W) #1~9 |  |  | U32 | 3,16 | 2 | 9
7410 | backlight off time |  |  | U16 | 3,16 | 1 | 1
7411 | brightness |  |  | U16 | 3,16 | 1 | 1
7412 | auto rotation |  |  | U16 | 3,16 | 1 | 1
7413 | Time Zone (~720 ~ 720) | 분단위 |  | S16 | 3,16 | 1 | 1
7414 | max/min reset period | 0: daily 1: weekly 2: monthly |  | U16 | 3,16 | 1 | 1
7415 | TEST MODE | 0 : not use, 1 : use |  | U16 | 3,16 | 1 | 1
7416 | TEST MODE INTERVAL |  |  | U16 | 3,16 | 1 | 1
7417 |  |  |  | U16 |  | 1 | 1
IOM SETTING
7418 | type |  |  | U16 | 3,16 | 1 | 1
7419 | reserved |  |  | U16 | 3,16 | 1 | 1
7420 | DI TYPE #0~3 | 0 : DI, 1 : PI |  | U16 | 3,16 | 1 | 4
7424 | DI debounce #0~3 | 4~255ms |  | U16 | 3,16 | 1 | 4
7428 | PI Scale #0~3 |  |  | U16 | 3,16 | 1 | 4
7432 | reserved |  |  | U16 | 3,16 | 1 | 14
Command
7446 | UTC Time |  |  | U16 | 3,16 | 1 | 4
7450 |  |  |  | U16 | 3,16 | 1 | 6
7456 | reboot | 0x1234 |  | U16 | 6 | 1 | 1
7457 | save settings | 0x1234 |  | U16 | 6 | 1 | 1
7458 | Calibration command all, #1~9 | 0: Enable Calibration 1: U gain 2: I gain 3: W gain 4: Ph gain 5: clear V 6: clear I 7: clear W 8: clear phase 9: IN gain 10: clear IN 11: Disable Calibration 12: save Calibration 13: Upp gain 14: clear Upp gain 15: set dcos 16: clear DcOffset 17: --- 18: --- |  | U16 | 6 | 1 | 10
7468 | V-ref, 1=1V #1~9 |  |  | U16 | 6 | 1 | 1
7469 | I-ref, 1=0.1A #1~9 |  |  | U16 | 6 | 1 | 1
7470 | In-ref, 1=0.1 #1~9 |  |  | U16 | 6 | 1 | 1
7471 | init settings | 0x1234 |  | U16 | 6 | 1 | 1
7472 | clear PI | 0x1234 |  | U16 | 6 | 1 | 1
7473 | clear demand ALL,#1~9 | 0x1234 |  | U16 | 6 | 1 | 10
7483 | clear minmax ALL,#1~9 | 0x1234 |  | U16 | 6 | 1 | 10
7493 | clear energy ALL,#1~9 | 0x1234 |  | U16 | 6 | 1 | 10
7503 | clear alarm ALL,#1~9 | 0x1234 |  | U16 | 6 | 1 | 10
7513 | clear event ALL,#1~9 | 0x1234 |  | U16 | 6 | 1 | 10
7523 | load event ALL,#1~9 | 1: down, 2:up, 3:top |  | U16 | 6 | 1 | 10
7533 | load alarm ALL,#1~9 | 1: down, 2:up, 3:top |  | U16 | 6 | 1 | 10
7543 | Alarm Ack ALL,#1~9 | not used |  | U16 | 6 | 1 | 10
7553 | Event Ack ALL,#1~9 | not used |  | U16 | 6 | 1 | 10
7563 | load itic #1~3 | 1: down, 2:up, 3:top |  | U16 | 6 | 1 | 3
7566 | load itic2 #1~3 | 1: down, 2:up, 3:top |  | U16 | 6 | 1 | 3
7569 | clear ITIC ALL,#1~3 | 0x1234 |  | U16 | 6 | 1 | 4
7573 | reserved |  |  | U16 | 6 | 1

## #1CH modbus
address | name | 설명 | Unit | TYPE | FC | Word Count | Item Count
Metering
0 | Time Stamp |  |  | UTC | 3 | 2 | 1
2 | TYPE |  |  | U16 | 3 | 1 | 1
3 | STATUS | 1 : online, 0 : offline |  | U16 | 3 | 1 | 1
4 | Frequency | 라인주파수 | Hz | float | 3 | 2 | 1
6 | Internal Temp |  | ℃ | float | 3 | 2 | 1
8 | U1 | 상전압 1 | V | float | 3 | 2 | 1
10 | U2 | 상전압 2 |  | float | 3 | 2 | 1
12 | U3 | 상전압 3 |  | float | 3 | 2 | 1
14 | U~ | 상전압 평균 |  | float | 3 | 2 | 1
16 | U12 | 선간 전압 12 |  | float | 3 | 2 | 1
18 | U23 | 선간 전압 23 |  | float | 3 | 2 | 1
20 | U31 | 선간 전압 31 |  | float | 3 | 2 | 1
22 | Upp~ | 선간 전압 평균 |  | float | 3 | 2 | 1
24 | Uunbalance2 |  | % | float | 3 | 2 | 1 | Uu=neg/pos*100
26 | Uunbalance0 |  |  | float | 3 | 2 | 1 | Uo=zero/pos*100
28 | U Zero Sequence Mag. |  |  | float | 3 | 2 | 1
30 | U Zero Sequence angle |  |  | float | 3 | 2 | 1
32 | U Positive Sequence Mag. |  |  | float | 3 | 2 | 1
34 | U Positive Sequence angle |  |  | float | 3 | 2 | 1
36 | U Negative Sequence Mag |  |  | float | 3 | 2 | 1
38 | U Negative Sequence angle |  |  | float | 3 | 2 | 1
40 | Angle U1 |  |  | float | 3 | 2 | 1
42 | Angle U2 |  |  | float | 3 | 2 | 1
44 | Angle U3 |  |  | float | 3 | 2 | 1
46 | U Underdeviation L1 |  | % | float | 3 | 2 | 1
48 | U Underdeviation L2 |  | % | float | 3 | 2 | 1
50 | U Underdeviation L3 |  | % | float | 3 | 2 | 1
52 | U Overdeviation L1 |  | % | float | 3 | 2 | 1
54 | U Overdeviation L2 |  | % | float | 3 | 2 | 1
56 | U Overdeviation L3 |  | % | float | 3 | 2 | 1
58 | I1 | 상전류 1 | A | float | 3 | 2 | 1
60 | I2 | 상전류 2 |  | float | 3 | 2 | 1
62 | I3 | 상전류 3 |  | float | 3 | 2 | 1
64 | I~ |  |  | float | 3 | 2 | 1
66 | I total (I1+I2+I3) |  |  | float | 3 | 2 | 1
68 | In(Measured) |  |  | float | 3 | 2 | 1 | 1. 5A: -3P4W(In) -3P3W(Ig), 2. AT/VT: Ig로 사용
70 | In(Calculated) | Ia+Ib+Ic+In = Ig |  | float | 3 | 2 | 1 | 1. 5A: -3P4W(Ig=Ia+Ib+Ic+In), -3P3W(Ig=Ia+Ib+Ic), 2. AT/VT: 5A와 동일
72 | Ig |  |  | float | 3 | 2 | 1
74 | I Zero Sequence Mag |  |  | float | 3 | 2 | 1
76 | I Zero Sequence angle |  |  | float | 3 | 2 | 1
78 | I Positive Sequence Mag. |  |  | float | 3 | 2 | 1
80 | I Positive Sequence angle |  |  | float | 3 | 2 | 1
82 | I Negative Sequence Mag. |  |  | float | 3 | 2 | 1
84 | I Negative Sequence angle |  |  | float | 3 | 2 | 1
86 | Angle I1 |  |  | float | 3 | 2 | 1
88 | Angle I2 |  |  | float | 3 | 2 | 1
90 | Angle I3 |  |  | float | 3 | 2 | 1
92 | Iunbalance2 |  | % | float | 3 | 2 | 1
94 | Iunbalance0 |  |  | float | 3 | 2 | 1
96 | P1 | 유효전력 P1 | W | float | 3 | 2 | 1
98 | P2 | 유효전력 P2 |  | float | 3 | 2 | 1
100 | P3 | 유효전력 P3 |  | float | 3 | 2 | 1
102 | P total | 유효전력 P-total |  | float | 3 | 2 | 1
104 | fP1 |  |  | float | 3 | 2 | 1
106 | fP2 |  |  | float | 3 | 2 | 1
108 | fP3 |  |  | float | 3 | 2 | 1
110 | fP total |  |  | float | 3 | 2 | 1
112 | Q1 | 무효전력 Q1 | VAR | float | 3 | 2 | 1
114 | Q2 | 무효전력 Q2 |  | float | 3 | 2 | 1
116 | Q3 | 무효전력 Q3 |  | float | 3 | 2 | 1
118 | Q total | 무효전력 Q-total |  | float | 3 | 2 | 1
120 | fQ1 |  |  | float | 3 | 2 | 1
122 | fQ2 |  |  | float | 3 | 2 | 1
124 | fQ3 |  |  | float | 3 | 2 | 1
126 | fQ total |  |  | float | 3 | 2 | 1
128 | S1 | 피상전력 S1 | VA | float | 3 | 2 | 1
130 | S2 | 피상전력 S2 |  | float | 3 | 2 | 1
132 | S3 | 피상전력 S3 |  | float | 3 | 2 | 1
134 | S total | 피상전력 S-total |  | float | 3 | 2 | 1
136 | fS1 |  |  | float | 3 | 2 | 1
138 | fS2 |  |  | float | 3 | 2 | 1
140 | fS3 |  |  | float | 3 | 2 | 1
142 | fS total |  |  | float | 3 | 2 | 1
144 | PF1 | 역률 PF1 | % | float | 3 | 2 | 1
146 | PF2 | 역률 PF2 |  | float | 3 | 2 | 1
148 | PF3 | 역률 PF3 |  | float | 3 | 2 | 1
150 | PF total | 역률 PF-total |  | float | 3 | 2 | 1
152 | dPF1 |  | % | float | 3 | 2 | 1
154 | dPF2 |  |  | float | 3 | 2 | 1
156 | dPF3 |  |  | float | 3 | 2 | 1
158 | dPF total |  |  | float | 3 | 2 | 1
160 | deformed Power D L1 |  | W | float | 3 | 2 | 1 | S=sqrt {P^{2}+Q^{2}+D^{2}}
162 | deformed Power D L2 |  |  | float | 3 | 2 | 1
164 | deformed Power D L3 |  |  | float | 3 | 2 | 1
166 | deformed Power D Total |  |  | float | 3 | 2 | 1
168 | Power Angle(atan(fPt,fQt) L1 |  | Degree | float | 3 | 2 | 1 | Angle between fundamental phase voltage and phase current
170 | Power Angle(atan(fPt,fQt) L2 |  |  | float | 3 | 2 | 1
172 | Power Angle(atan(fPt,fQt) L3 |  |  | float | 3 | 2 | 1
174 |  |  |  | float | 3 | 2 | 1
176 | THD V1 |  | % | float | 3 | 2 | 1
178 | THD V2 |  |  | float | 3 | 2 | 1 | Chip에서 제공하는 결과 사용
180 | THD V3 |  |  | float | 3 | 2 | 1
182 | THD V12 |  |  | float | 3 | 2 | 1
184 | THD V23 |  |  | float | 3 | 2 | 1
186 | THD V31 |  |  | float | 3 | 2 | 1
188 | CF V1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
190 | CF V2 |  |  | float | 3 | 2 | 1
192 | CF V3 |  |  | float | 3 | 2 | 1
194 | CF V12 |  |  | float | 3 | 2 | 1
196 | CF V23 |  |  | float | 3 | 2 | 1
198 | CF V31 |  |  | float | 3 | 2 | 1
200 | THD I1 |  |  | float | 3 | 2 | 1
202 | THD I2 |  |  | float | 3 | 2 | 1
204 | THD I3 |  |  | float | 3 | 2 | 1
206 | TDD I1 |  |  | float | 3 | 2 | 1
208 | TDD I2 |  |  | float | 3 | 2 | 1
210 | TDD I3 |  |  | float | 3 | 2 | 1
212 | K I1 | K-FACTOR : 고조파 허용율 |  | float | 3 | 2 | 1
214 | K I2 |  |  | float | 3 | 2 | 1
216 | K I3 |  |  | float | 3 | 2 | 1
218 | CF I1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
220 | CF I2 |  |  | float | 3 | 2 | 1
222 | CF I3 |  |  | float | 3 | 2 | 1
224 | fU1 | 기본파 U1 | V | float | 3 | 2 | 1
226 | fU2 | 기본파 U2 |  | float | 3 | 2 | 1
228 | fU3 | 기본파 U3 |  | float | 3 | 2 | 1
230 | fU~ | 기본파 전압 평균 |  | float | 3 | 2 | 1
232 | fI1 | 기본파 I1 | A | float | 3 | 2 | 1
234 | fI2 | 기본파 I2 |  | float | 3 | 2 | 1
236 | fI3 | 기본파 I3 |  | float | 3 | 2 | 1
238 | fI~ | 기본파 전류 평균 |  | float | 3 | 2 | 1
Energy
240 | import kwh(0 ~ 999,999,999.9 kw) TOTAL | 누적 TOTAL 유효전력량 |  | U32 | 3 | 2 | 1
242 | export kwh TOTAL |  |  | U32 | 3 | 2 | 1
244 | import kvarh TOTAL |  |  | U32 | 3 | 2 | 1
246 | export kvarh TOTAL |  |  | U32 | 3 | 2 | 1
248 | kvah TOTAL |  |  | U32 | 3 | 2 | 1
250 |  |  |  | U32 | 3 | 2 | 1
252 | import kwh(0 ~ 999,999,999.9 kw) L1 | 누적 L1 유효전력량 |  | U32 | 3 | 2 | 1
254 | export kwh L1 |  |  | U32 | 3 | 2 | 1
256 | import kvarh L1 |  |  | U32 | 3 | 2 | 1
258 | export kvarh L1 |  |  | U32 | 3 | 2 | 1
260 | kvah L1 |  |  | U32 | 3 | 2 | 1
262 |  |  |  | U32 | 3 | 2 | 1
264 | import kwh(0 ~ 999,999,999.9 kw) L2 | 누적 L2 유효전력량 |  | U32 | 3 | 2 | 1
266 | export kwh L2 |  |  | U32 | 3 | 2 | 1
268 | import kvarh L2 |  |  | U32 | 3 | 2 | 1
270 | export kvarh L2 |  |  | U32 | 3 | 2 | 1
272 | kvah L2 |  |  | U32 | 3 | 2 | 1
274 |  |  |  | U32 | 3 | 2 | 1
276 | import kwh(0 ~ 999,999,999.9 kw) L3 | 누적 L3 유효전력량 |  | U32 | 3 | 2 | 1
278 | export kwh L3 |  |  | U32 | 3 | 2 | 1
280 | import kvarh L3 |  |  | U32 | 3 | 2 | 1
282 | export kvarh L3 |  |  | U32 | 3 | 2 | 1
284 | kvah L3 |  |  | U32 | 3 | 2 | 1
286 |  |  |  | U32 | 3 | 2 | 1
288 | import kwh this month TOTAL | TOTAL THIS MONTH |  | U32 | 3 | 2 | 1
290 | export kwh this month TOTAL |  |  | U32 | 3 | 2 | 1
292 | import kvarh this month TOTAL |  |  | U32 | 3 | 2 | 1
294 | export kvarh this month TOTAL |  |  | U32 | 3 | 2 | 1
296 | kvah this month TOTAL |  |  | U32 | 3 | 2 | 1
298 |  |  |  | U32 | 3 | 2 | 1
300 | import kwh this month L1 | L1 THIS MONTH |  | U32 | 3 | 2 | 1
302 | export kwh this month L1 |  |  | U32 | 3 | 2 | 1
304 | import kvarh this month L1 |  |  | U32 | 3 | 2 | 1
306 | export kvarh this month L1 |  |  | U32 | 3 | 2 | 1
308 | kvah this month L1 |  |  | U32 | 3 | 2 | 1
310 |  |  |  | U32 | 3 | 2 | 1
312 | import kwh this month L2 | L2 THIS MONTH |  | U32 | 3 | 2 | 1
314 | export kwh this month L2 |  |  | U32 | 3 | 2 | 1
316 | import kvarh this month L2 |  |  | U32 | 3 | 2 | 1
318 | export kvarh this month L2 |  |  | U32 | 3 | 2 | 1
320 | kvah this month L2 |  |  | U32 | 3 | 2 | 1
322 |  |  |  | U32 | 3 | 2 | 1
324 | import kwh this month L3 | L3 THIS MONTH |  | U32 | 3 | 2 | 1
326 | export kwh this month L3 |  |  | U32 | 3 | 2 | 1
328 | import kvarh this month L3 |  |  | U32 | 3 | 2 | 1
330 | export kvarh this month L3 |  |  | U32 | 3 | 2 | 1
332 | kvah this month L3 |  |  | U32 | 3 | 2 | 1
334 |  |  |  | U32 | 3 | 2 | 1
336 | import kwh last month TOTAL | TOTAL LAST MONTH |  | U32 | 3 | 2 | 1
338 | export kwh last month |  |  | U32 | 3 | 2 | 1
340 | import kvarh last month |  |  | U32 | 3 | 2 | 1
342 | export kvarh last month |  |  | U32 | 3 | 2 | 1
344 | kvah last month |  |  | U32 | 3 | 2 | 1
346 |  |  |  | U32 | 3 | 2 | 1
348 | import kwh last month L1 | L1 LAST MONTH |  | U32 | 3 | 2 | 1
350 | export kwh last month |  |  | U32 | 3 | 2 | 1
352 | import kvarh last month |  |  | U32 | 3 | 2 | 1
354 | export kvarh last month |  |  | U32 | 3 | 2 | 1
356 | kvah last month |  |  | U32 | 3 | 2 | 1
358 |  |  |  | U32 | 3 | 2 | 1
360 | import kwh last month L2 | L2 LAST MONTH |  | U32 | 3 | 2 | 1
362 | export kwh last month |  |  | U32 | 3 | 2 | 1
364 | import kvarh last month |  |  | U32 | 3 | 2 | 1
366 | export kvarh last month |  |  | U32 | 3 | 2 | 1
368 | kvah last month |  |  | U32 | 3 | 2 | 1
370 |  |  |  | U32 | 3 | 2 | 1
372 | import kwh last month L3 | L3 LAST MONTH |  | U32 | 3 | 2 | 1
374 | export kwh last month |  |  | U32 | 3 | 2 | 1
376 | import kvarh last month |  |  | U32 | 3 | 2 | 1
378 | export kvarh last month |  |  | U32 | 3 | 2 | 1
380 | kvah last month |  |  | U32 | 3 | 2 | 1
382 |  |  |  | U32 | 3 | 2 | 1
384 | import kwh | TOTAL,L1,L2,L3 |  | U64 | 3 | 4 | 4
400 | export kwh |  |  | U64 | 3 | 4 | 4
416 | import kvarh |  |  | U64 | 3 | 4 | 4
432 | export kvarh |  |  | U64 | 3 | 4 | 4
448 | kvah |  |  | U64 | 3 | 4 | 4
464 |  |  |  | U64 | 3 | 4 | 4
Demand
480 | Time Stamp |  |  | UTC | 3 | 2 | 1
482 | Max Demand P(import) |  |  | float | 3 | 2 | 1
484 | Time Stamp |  |  | UTC | 3 | 2 | 1
486 | Max Demand P(export) |  |  | float | 3 | 2 | 1
488 | Time Stamp |  |  | UTC | 3 | 2 | 1
490 | Max Demand Q(import) |  |  | float | 3 | 2 | 1
492 | Time Stamp |  |  | UTC | 3 | 2 | 1
494 | Max Demand Q(export) |  |  | float | 3 | 2 | 1
496 | Time Stamp |  |  | UTC | 3 | 2 | 1
498 | Max Demand S |  |  | float | 3 | 2 | 1
500 | Time Stamp |  |  | UTC | 3 | 2 | 1
502 | Max Demand I1 |  |  | float | 3 | 2 | 1
504 | Time Stamp |  |  | UTC | 3 | 2 | 1
506 | Max Demand I2 |  |  | float | 3 | 2 | 1
508 | Time Stamp |  |  | UTC | 3 | 2 | 1
510 | Max Demand I3 |  |  | float | 3 | 2 | 1
512 | Demand time stamp |  |  | UTC | 3 | 2 | 1
514 | Demand P(import) |  |  | float | 3 | 2 | 1
516 | Demand P(export) |  |  | float | 3 | 2 | 1 | 최근 24시간 그래프 그린다
518 | Demand Q(import) |  |  | float | 3 | 2 | 1
520 | Demand Q(export) |  |  | float | 3 | 2 | 1
522 | Demand S(export) |  |  | float | 3 | 2 | 1
524 | Demand I1 |  |  | float | 3 | 2 | 1
526 | Demand I2 |  |  | float | 3 | 2 | 1
528 | Demand I3 |  |  | float | 3 | 2 | 1
530 | Present Demand P(import) |  |  | float | 3 | 2 | 1
532 | Present Demand P(export) |  |  | float | 3 | 2 | 1
534 | Present Demand Q(import) |  |  | float | 3 | 2 | 1
536 | Present Demand Q(export) |  |  | float | 3 | 2 | 1
538 | Present Demand S(export) |  |  | float | 3 | 2 | 1
540 | Forecast Demand P(export) |  |  | float | 3 | 2 | 1
542 | Demand P 15m(import) |  |  | float | 3 | 2 | 1
544 |  |  |  | float | 3 | 2 | 1
546 |  |  |  | float | 3 | 2 | 1
548 | Time Stamp(Demand Log 시작일) |  |  | U32 | 3 | 2 | 1
550 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
742 |  |  |  | float | 3 | 2 | 19
Voltage Quality RealTime Value
780 | Voltage Under Deviation L1 |  | % | float | 3 | 2 | 1
782 | Voltage Under Deviation L2 |  | % | float | 3 | 2 | 1
784 | Voltage Under Deviation L3 |  | % | float | 3 | 2 | 1
786 | Voltage Under Value L1 |  | rms | float | 3 | 2 | 1
788 | Voltage Under Value L2 |  | rms | float | 3 | 2 | 1
790 | Voltage Under Value L3 |  | rms | float | 3 | 2 | 1
792 | Voltage Over Deviation L1 |  | % | float | 3 | 2 | 1
794 | Voltage Over Deviation L2 |  | % | float | 3 | 2 | 1
796 | Voltage Over Deviation L3 |  | % | float | 3 | 2 | 1
798 | Voltage Over Value L1 |  | rms | float | 3 | 2 | 1
800 | Voltage Over Value L2 |  | rms | float | 3 | 2 | 1
802 | Voltage Over Value L3 |  | rms | float | 3 | 2 | 1
804 | Flickers Pi L1 | 150/180 Cycles |  | float | 3 | 2 | 1
806 | Flickers Pi L2 |  |  | float | 3 | 2 | 1
808 | Flickers Pi L3 |  |  | float | 3 | 2 | 1
810 | Flicker Pst L1 | 10min |  | float | 3 | 2 | 1
812 | Flicker Pst L2 |  |  | float | 3 | 2 | 1
814 | Flicker Pst L3 |  |  | float | 3 | 2 | 1
816 | Flicker Plt L1 | 2hr |  | float | 3 | 2 | 1 | 최근 24시간 그래프 그린다
818 | Flicker Plt L2 |  |  | float | 3 | 2 | 1
820 | Flicker Plt L3 |  |  | float | 3 | 2 | 1
822 | Signaling Volt L1 | Magnitude of current 10/12 cycles as a percentage of nominal voltage. |  | float | 3 | 2 | 1
824 | Signaling Volt L2 |  |  | float | 3 | 2 | 1
826 | Signaling Volt L3 |  |  | float | 3 | 2 | 1
828 | Signaling Volt Max L1 | Maximum magnitude of MSV from recording started as a percentage of nominal voltage |  | float | 3 | 2 | 1
830 | Signaling Volt Max L2 |  |  | float | 3 | 2 | 1
832 | Signaling Volt Max L3 |  |  | float | 3 | 2 | 1
834 |  |  |  | float | 3 | 2 | 23
EN50160 This Week
880 | start date |  |  | UTC | 3 | 2 | 1
882 | end date |  |  | UTC | 3 | 2 | 1
884 | status&compliance | bit 0: Freq Var1 bit 1: Freq Var2 bit 2: Volt Var1 L1 bit 3: Volt Var1 L2 bit 4: Volt Var1 L3 bit 5: Volt Var2 L1 bit 6: Volt Var2 L2 bit 7: Volt Var2 L3 bit 8: Unbalance bit 9: Volt THD L1 bit 10: Volt THD L2 bit 11: Volt THD L3 bit 12: Volt HD L1 bit 13: Volt HD L2 bit 14: Volt HD L3 bit 15: Pst L1 bit 16: Pst L2 bit 17: Pst L3 bit 18: Plt L1 bit 19: Plt L2 bit 20: Plt L3 bit 21: SigVolt L1 bit 22: SigVolt L2 bit 23: SigVolt L3 bit 31: Complete [status] 0: OK 1: failed |  | U32 | 3 | 2 | 1
886 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1 | 95%/Week
887 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1 | Info Only
888 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
889 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
890 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
891 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
892 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
893 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1 | Info Only
894 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
895 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
896 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
897 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
898 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
899 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
900 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
901 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
902 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
903 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
904 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
905 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
906 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
907 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
908 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
909 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
910 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
911 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1 | 99%/Day
912 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
913 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
914 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
915 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
916 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
917 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
918 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
919 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
920 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
921 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
922 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
923 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
924 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
925 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
926 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
927 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
928 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
929 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
EN50160 Last Week
930 | start date |  |  | UTC | 3 | 2 | 1
932 | end date |  |  | UTC | 3 | 2 | 1
934 | status |  |  | U16 | 3 | 1 | 1
935 | compilance |  |  | U16 | 3 | 1 | 1
936 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1
937 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1
938 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
939 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
940 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1
941 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
942 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
943 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1
944 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
945 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
946 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1
947 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
948 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
949 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1
950 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
951 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
952 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1
953 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
954 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
955 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1
956 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
957 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
958 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1
959 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
960 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
961 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1
962 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
963 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
964 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
965 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
966 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
967 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
968 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
969 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
970 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
971 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
972 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
973 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
974 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
975 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
976 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
977 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
978 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
979 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
Harmonics
980 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
1044 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
1108 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
1172 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
1236 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
1300 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
1364 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
1428 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
1492 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
1556 |  |  |  | S16 | 3 | 1 | 24
Inter Harmonics
1580 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
1644 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
1708 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
1772 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
1836 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
1900 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
1964 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
2028 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
2092 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
2156 |  |  |  | S16 | 3 | 1 | 24
Max/Min
2180 | fr |  |  | U16 | 3 | 1 | 1
2181 | re |  |  | U16 | 3 | 1 | 1
2182 | Reset TimeStamp |  |  | UTC | 3 | 2 | 1
2184 | Frequency | Max |  | float | 3 | 2 | 1
2186 |  | Max Timestamp |  | UTC | 3 | 2 | 1
2188 |  | Min |  | float | 3 | 2 | 1
2190 |  | Min Timestamp |  | UTC | 3 | 2 | 1
2192 | Temp |  |  | float | 3 | 2 | 4
2200 | U1 |  |  | float | 3 | 2 | 4
2208 | U2 |  |  | float | 3 | 2 | 4
2216 | U3 |  |  | float | 3 | 2 | 4 | http://www.relaytech.com/symcomp_calculator.htm
2224 | U~ |  |  | float | 3 | 2 | 4
2232 | U12 |  |  | float | 3 | 2 | 4
2240 | U23 |  |  | float | 3 | 2 | 4
2248 | U31 |  |  | float | 3 | 2 | 4
2256 | Upp~ |  |  | float | 3 | 2 | 4
2264 | I1 |  |  | float | 3 | 2 | 4
2272 | I2 |  |  | float | 3 | 2 | 4
2280 | I3 |  |  | float | 3 | 2 | 4
2288 | I~ |  |  | float | 3 | 2 | 4
2296 | I total |  |  | float | 3 | 2 | 4
2304 | In |  |  | float | 3 | 2 | 4
2312 | Isum |  |  | float | 3 | 2 | 4
2320 | P1 |  |  | float | 3 | 2 | 4
2328 | P2 |  |  | float | 3 | 2 | 4
2336 | P3 |  |  | float | 3 | 2 | 4
2344 | P total |  |  | float | 3 | 2 | 4
2352 | Q1 |  |  | float | 3 | 2 | 4
2360 | Q2 |  |  | float | 3 | 2 | 4
2368 | Q3 |  |  | float | 3 | 2 | 4
2376 | Q total |  |  | float | 3 | 2 | 4
2384 | S1 |  |  | float | 3 | 2 | 4
2392 | S2 |  |  | float | 3 | 2 | 4
2400 | S3 |  |  | float | 3 | 2 | 4
2408 | S total |  |  | float | 3 | 2 | 4
2416 | PF L1 |  |  | float | 3 | 2 | 4
2424 | PF L2 |  |  | float | 3 | 2 | 4
2432 | PF L3 |  |  | float | 3 | 2 | 4
2440 | PF total |  |  | float | 3 | 2 | 4
2448 | THD U1 |  |  | float | 3 | 2 | 4
2456 | THD U2 |  |  | float | 3 | 2 | 4
2464 | THD U3 |  |  | float | 3 | 2 | 4
2472 | THD U12 |  |  | float | 3 | 2 | 4
2480 | THD U23 |  |  | float | 3 | 2 | 4
2488 | THD U31 |  |  | float | 3 | 2 | 4
2496 | THD I1 |  |  | float | 3 | 2 | 4
2504 | THD I2 |  |  | float | 3 | 2 | 4
2512 | THD I3 |  |  | float | 3 | 2 | 4
2520 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
2522 | reserved |  |  | U16 | 3 | 1 | 1
2523 | CRC |  |  | U16 | 3 | 1 | 1
2524 |  |  |  | U16 | 3 | 1 | 6
alarm status
2530 | fr |  |  | U16 | 3 | 1 | 1
2531 | re |  |  | U16 | 3 | 1 | 1
2532 | reset Ts |  |  | UTC | 3 | 2 | 1
2534 | Alarm State #1 | Alarm Channel |  | U16 | 3 | 1 | 1
2535 |  | Alarm Condition |  | U16 | 3 | 1 | 1
2536 |  | Alarm Level |  | float | 3 | 2 | 1
2538 |  | Alarm Status |  | U16 | 3 | 1 | 1
2539 |  | Alarm Count |  | U16 | 3 | 1 | 1
2540 | Alarm State #2 |  |  | U16 | 3 | 1 | 6
2546 | Alarm State #3 |  |  | U16 | 3 | 1 | 6
2552 | Alarm State #4 |  |  | U16 | 3 | 1 | 6
2558 | Alarm State #5 |  |  | U16 | 3 | 1 | 6
2564 | Alarm State #6 |  |  | U16 | 3 | 1 | 6
2570 | Alarm State #7 |  |  | U16 | 3 | 1 | 6
2576 | Alarm State #8 |  |  | U16 | 3 | 1 | 6
2582 | Alarm State #9 |  |  | U16 | 3 | 1 | 6
2588 | Alarm State #10 |  |  | U16 | 3 | 1 | 6
2594 | Alarm State #11 |  |  | U16 | 3 | 1 | 6
2600 | Alarm State #12 |  |  | U16 | 3 | 1 | 6
2606 | Alarm State #13 |  |  | U16 | 3 | 1 | 6
2612 | Alarm State #14 |  |  | U16 | 3 | 1 | 6
2618 | Alarm State #15 |  |  | U16 | 3 | 1 | 6
2624 | Alarm State #16 |  |  | U16 | 3 | 1 | 6
2630 | Alarm State #17 |  |  | U16 | 3 | 1 | 6
2636 | Alarm State #18 |  |  | U16 | 3 | 1 | 6
2642 | Alarm State #19 |  |  | U16 | 3 | 1 | 6
2648 | Alarm State #20 |  |  | U16 | 3 | 1 | 6
2654 | Alarm State #21 |  |  | U16 | 3 | 1 | 6
2660 | Alarm State #22 |  |  | U16 | 3 | 1 | 6
2666 | Alarm State #23 |  |  | U16 | 3 | 1 | 6
2672 | Alarm State #24 |  |  | U16 | 3 | 1 | 6
2678 | Alarm State #25 |  |  | U16 | 3 | 1 | 6
2684 | Alarm State #26 |  |  | U16 | 3 | 1 | 6
2690 | Alarm State #27 |  |  | U16 | 3 | 1 | 6
2696 | Alarm State #28 |  |  | U16 | 3 | 1 | 6
2702 | Alarm State #29 |  |  | U16 | 3 | 1 | 6
2708 | Alarm State #30 |  |  | U16 | 3 | 1 | 6
2714 | Alarm State #31 |  |  | U16 | 3 | 1 | 6
2720 | Alarm State #32 |  |  | U16 | 3 | 1 | 6
2726 | update Ts |  |  | U32 | 3 | 2 | 1
2728 | Global Alarm Status | (alarm 하나라도 있으면 1, 아니면 0) |  | U16 | 3 | 1 | 1
2729 |  |  |  | U16 | 3 | 1 | 1
alarm log
2730 | fr | 0 ~ 1023 |  | U16 | 3 | 1 | 1
2731 | re | 0 ~ 1023 |  | U16 | 3 | 1 | 1
2732 | count | 전체 log 수 |  | U16 | 3 | 1 | 1
2733 | seq |  |  | U16 | 3 | 1 | 1
2734 | Alarm Log #1 | Time Stamp |  | UTC | 3 | 2 | 1 | 2019-5-11변경
2736 |  | status |  | U16 | 3 | 1 | 1
2737 |  | Alarm Channel & Condition |  | U16 | 3 | 1 | 1
2738 |  | level |  | float | 3 | 2 | 1
2740 |  | Value |  | float | 3 | 2 | 1
2742 | Alarm Log #2 |  |  | U16 | 3 | 1 | 8
2750 | Alarm Log #3 |  |  | U16 | 3 | 1 | 8
2758 | Alarm Log #4 |  |  | U16 | 3 | 1 | 8
2766 | Alarm Log #5 |  |  | U16 | 3 | 1 | 8
2774 | Alarm Log #6 |  |  | U16 | 3 | 1 | 8
2782 | Alarm Log #7 |  |  | U16 | 3 | 1 | 8
2790 | Alarm Log #8 |  |  | U16 | 3 | 1 | 8
2798 | Alarm Log #9 |  |  | U16 | 3 | 1 | 8
2806 | Alarm Log #10 |  |  | U16 | 3 | 1 | 8
2814 | Alarm Log #11 |  |  | U16 | 3 | 1 | 8
2822 | Alarm Log #12 |  |  | U16 | 3 | 1 | 8
2830 | Alarm Log #13 |  |  | U16 | 3 | 1 | 8
2838 | Alarm Log #14 |  |  | U16 | 3 | 1 | 8
2846 | Alarm Log #15 |  |  | U16 | 3 | 1 | 8
2854 | Alarm Log #16 |  |  | U16 | 3 | 1 | 8
2862 | Alarm Log #17 |  |  | U16 | 3 | 1 | 8
2870 | Alarm Log #18 |  |  | U16 | 3 | 1 | 8
2878 | Alarm Log #19 |  |  | U16 | 3 | 1 | 8
2886 | Alarm Log #20 |  |  | U16 | 3 | 1 | 8
2894 | Alarm Log #21 |  |  | U16 | 3 | 1 | 8
2902 | Alarm Log #22 |  |  | U16 | 3 | 1 | 8
2910 | Alarm Log #23 |  |  | U16 | 3 | 1 | 8
2918 | Alarm Log #24 |  |  | U16 | 3 | 1 | 8
2926 | Alarm Log #25 |  |  | U16 | 3 | 1 | 8
2934 | Alarm Log #26 |  |  | U16 | 3 | 1 | 8
2942 | Alarm Log #27 |  |  | U16 | 3 | 1 | 8
2950 | Alarm Log #28 |  |  | U16 | 3 | 1 | 8
2958 | Alarm Log #29 |  |  | U16 | 3 | 1 | 8
2966 | Alarm Log #30 |  |  | U16 | 3 | 1 | 8
2974 | Alarm Log #31 |  |  | U16 | 3 | 1 | 8
2982 | Alarm Log #32 |  |  | U16 | 3 | 1 | 8
2990 |  |  |  | U16 | 3 | 1 | 40
이벤트 리스트
3030 | fr | 0 ~ 1023 |  | U16 | 3 | 1 | 1
3031 | re | 0 ~ 1023 |  | U16 | 3 | 1 | 1
3032 | count | 0 ~ 1023 |  | U16 | 3 | 1 | 1
3033 | seq |  |  | U16 | 3 | 1 | 1
PQ 이벤트(Sag, Swell, Transient, OC)
3034 | start ts |  |  | UTC | 3 | 2 | 1
3036 | start ts(ms) |  |  | U16 | 3 | 1 | 1
3037 | duration |  |  | U16 | 3 | 1 | 1
3038 | type | 1 : E_SAG 2 : E_SWELL 3 : E_sINTR 4 : E_lINTR 5 : E_OC 6 : E_RVC 7 : E_TrV 8 : E_TrC |  | U16 | 3 | 1 | 1
3039 | mask |  |  | U16 | 3 | 1 | 1
3040 | Level 1 |  |  | float | 3 | 2 | 1
3042 | Level 2 |  |  | float | 3 | 2 | 1
3044 | Level 3 |  |  | float | 3 | 2 | 1
3046 | PQ Event #2 |  |  | U16 | 3 | 1 | 12
3058 | PQ Event #3 |  |  | U16 | 3 | 1 | 12
3070 | PQ Event #4 |  |  | U16 | 3 | 1 | 12
3082 | PQ Event #5 |  |  | U16 | 3 | 1 | 12
3094 | PQ Event #6 |  |  | U16 | 3 | 1 | 12
3106 | PQ Event #7 |  |  | U16 | 3 | 1 | 12
3118 | PQ Event #8 |  |  | U16 | 3 | 1 | 12
3130 | PQ Event #9 |  |  | U16 | 3 | 1 | 12
3142 | PQ Event #10 |  |  | U16 | 3 | 1 | 12
3154 | PQ Event #11 |  |  | U16 | 3 | 1 | 12
3166 | PQ Event #12 |  |  | U16 | 3 | 1 | 12
3178 | PQ Event #13 |  |  | U16 | 3 | 1 | 12
3190 | PQ Event #14 |  |  | U16 | 3 | 1 | 12
3202 | PQ Event #15 |  |  | U16 | 3 | 1 | 12
3214 | PQ Event #16 |  |  | U16 | 3 | 1 | 12
3226 | PQ Event #17 |  |  | U16 | 3 | 1 | 12
3238 | PQ Event #18 |  |  | U16 | 3 | 1 | 12
3250 | PQ Event #19 |  |  | U16 | 3 | 1 | 12
3262 | PQ Event #20 |  |  | U16 | 3 | 1 | 12
3274 | PQ Event #21 |  |  | U16 | 3 | 1 | 12
3286 | PQ Event #22 |  |  | U16 | 3 | 1 | 12
3298 | PQ Event #23 |  |  | U16 | 3 | 1 | 12
3310 | PQ Event #24 |  |  | U16 | 3 | 1 | 12
3322 | PQ Event #25 |  |  | U16 | 3 | 1 | 12
3334 | PQ Event #26 |  |  | U16 | 3 | 1 | 12
3346 | PQ Event #27 |  |  | U16 | 3 | 1 | 12
3358 | PQ Event #28 |  |  | U16 | 3 | 1 | 12
3370 | PQ Event #29 |  |  | U16 | 3 | 1 | 12
3382 | PQ Event #30 |  |  | U16 | 3 | 1 | 12
3394 | PQ Event #31 |  |  | U16 | 3 | 1 | 12
3406 | PQ Event #32 |  |  | U16 | 3 | 1 | 12
3418 |  |  |  | U16 | 3 | 1 | 2
PQ Event Counter
3420 |  |  |  | U16 | 3 | 1 | 1
3421 |  |  |  | U16 | 3 | 1 | 1
3422 |  |  |  | U16 | 3 | 1 | 1
3423 | Sag Coount |  |  | U16 | 3 | 1 | 1
3424 | Swell Count |  |  | U16 | 3 | 1 | 1
3425 |  |  |  | U16 | 3 | 1 | 1
3426 |  |  |  | U16 | 3 | 1 | 1
3427 |  |  |  | U16 | 3 | 1 | 1
3428 |  |  |  | U16 | 3 | 1 | 1
3429 |  |  |  | U16 | 3 | 1 | 1
Wave Sample | [7 empty] | 32K: 67,107,786 8K: 74,518,668 첫번째 번지 접근시 wave data를 modbus map으로 load 한다
3430 | Wave Form V1 (160 sample) |  |  | S16 | 3 | 1 | 160
3590 | Wave Form V2 (160 sample) |  |  | S16 | 3 | 1 | 160
3750 | Wave Form V3 (160 sample) |  |  | S16 | 3 | 1 | 160
3910 | Wave Form V12 (160 sample) |  |  | S16 | 3 | 1 | 160
4070 | Wave Form V23 (160 sample) |  |  | S16 | 3 | 1 | 160
4230 | Wave Form V31 (160 sample) |  |  | S16 | 3 | 1 | 160
4390 | Wave Form I1 (160 sample) |  |  | S16 | 3 | 1 | 160
4550 | Wave Form I2 (160 sample) |  |  | S16 | 3 | 1 | 160
4710 | Wave Form I3 (160 sample) |  |  | S16 | 3 | 1 | 160
4870 | vscale |  |  | float | 3 | 2 | 1
4872 | iscale |  |  | float | 3 | 2 | 1
4874 |  |  |  | S16 | 3 | 1 | 6
월간리포트 생성위한 10분 평균
4880 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
4882 | U1 |  |  | float | 3 | 2 | 1
4884 | U2 |  |  | float | 3 | 2 | 1
4886 | U3 |  |  | float | 3 | 2 | 1
4888 | U THD1 |  |  | float | 3 | 2 | 1
4890 | U THD2 |  |  | float | 3 | 2 | 1
4892 | U THD3 |  |  | float | 3 | 2 | 1
4894 | Upp THD1 |  |  | float | 3 | 2 | 1
4896 | Upp THD2 |  |  | float | 3 | 2 | 1
4898 | Upp THD3 |  |  | float | 3 | 2 | 1
4900 | U Unbal Uu |  |  | float | 3 | 2 | 1
4902 | U Unbal Uo |  |  | float | 3 | 2 | 1
4904 | I1 |  |  | float | 3 | 2 | 1
4906 | I2 |  |  | float | 3 | 2 | 1
4908 | I3 |  |  | float | 3 | 2 | 1
4910 | In |  |  | float | 3 | 2 | 1
4912 | I THD1 |  |  | float | 3 | 2 | 1
4914 | I THD2 |  |  | float | 3 | 2 | 1
4916 | I THD3 |  |  | float | 3 | 2 | 1
4918 | I TDD1 |  |  | float | 3 | 2 | 1
4920 | I TDD2 |  |  | float | 3 | 2 | 1
4922 | I TDD3 |  |  | float | 3 | 2 | 1
4924 | K-factor 1 |  |  | float | 3 | 2 | 1
4926 | K-factor 2 |  |  | float | 3 | 2 | 1
4928 | K-factor 3 |  |  | float | 3 | 2 | 1
4930 | I Unbal Iu |  |  | float | 3 | 2 | 1
4932 | I Unbal Io |  |  | float | 3 | 2 | 1
4934 | kw imp |  |  | float | 3 | 2 | 1
4936 | kw exp |  |  | float | 3 | 2 | 1
4938 | kvar lag |  |  | float | 3 | 2 | 1
4940 | kvar lead |  |  | float | 3 | 2 | 1
4942 | kVA |  |  | float | 3 | 2 | 1
4944 | PF |  |  | float | 3 | 2 | 1
4946 | dPF |  |  | float | 3 | 2 | 1
4948 | temperature #1 |  |  | float | 3 | 2 | 1
4950 | temperature #2 |  |  | float | 3 | 2 | 1
4952 | temperature #3 |  |  | float | 3 | 2 | 1
4954 | temperature #4 |  |  | float | 3 | 2 | 1
4956 | temperature #5 |  |  | float | 3 | 2 | 1 | *통신이 끊어진 경우 복구를 위해 사용된다
4958 | Harmonics V1 |  |  | S16 | 3 | 1 | 24
4982 | Harmonics V2 |  |  | S16 | 3 | 1 | 24 | demand
5006 | Harmonics V3 |  |  | S16 | 3 | 1 | 24
5030 | Harmonics V12 |  |  | S16 | 3 | 1 | 24
5054 | Harmonics V23 |  |  | S16 | 3 | 1 | 24
5078 | Harmonics V31 |  |  | S16 | 3 | 1 | 24
5102 | Harmonics I1 |  |  | S16 | 3 | 1 | 24
5126 | Harmonics I2 |  |  | S16 | 3 | 1 | 24
5150 | Harmonics I3 |  |  | S16 | 3 | 1 | 24
5174 |  |  |  | U16 | 3 | 1 | 6
Energy log
5180 | Time Stamp |  |  | UTC | 3 | 2 | 1
5182 | kwh import |  |  | float | 3 | 2 | 1
5184 | kvarh lag |  |  | float | 3 | 2 | 1
5186 | kvarh lead |  |  | float | 3 | 2 | 1
5188 | kVAh |  |  | float | 3 | 2 | 1
5190 | energy log last day 01h |  |  | float | 3 | 2 | 4
5198 | energy log last day 02h |  |  | float | 3 | 2 | 4
5206 | energy log last day 03h |  |  | float | 3 | 2 | 4
5214 | energy log last day 04h |  |  | float | 3 | 2 | 4
5222 | energy log last day 05h |  |  | float | 3 | 2 | 4
5230 | energy log last day 06h |  |  | float | 3 | 2 | 4
5238 | energy log last day 07h |  |  | float | 3 | 2 | 4
5246 | energy log last day 08h |  |  | float | 3 | 2 | 4
5254 | energy log last day 09h |  |  | float | 3 | 2 | 4
5262 | energy log last day 10h |  |  | float | 3 | 2 | 4
5270 | energy log last day 11h |  |  | float | 3 | 2 | 4
5278 | energy log last day 12h |  |  | float | 3 | 2 | 4
5286 | energy log last day 13h |  |  | float | 3 | 2 | 4
5294 | energy log last day 14h |  |  | float | 3 | 2 | 4
5302 | energy log last day 15h |  |  | float | 3 | 2 | 4
5310 | energy log last day 16h |  |  | float | 3 | 2 | 4
5318 | energy log last day 17h |  |  | float | 3 | 2 | 4
5326 | energy log last day 18h |  |  | float | 3 | 2 | 4
5334 | energy log last day 19h |  |  | float | 3 | 2 | 4
5342 | energy log last day 20h |  |  | float | 3 | 2 | 4
5350 | energy log last day 21h |  |  | float | 3 | 2 | 4
5358 | energy log last day 22h |  |  | float | 3 | 2 | 4
5366 | energy log last day 23h |  |  | float | 3 | 2 | 4
5374 |  |  |  | U16 | 3 | 1 | 6
5380 | Time Stamp |  |  | UTC | 3 | 2 | 1
5382 | kwh import |  |  | float | 3 | 2 | 1
5384 | kvarh lag |  |  | float | 3 | 2 | 1
5386 | kvarh lead |  |  | float | 3 | 2 | 1
5388 | kVAh |  |  | float | 3 | 2 | 1
5390 | energy log this day 01h |  |  | float | 3 | 2 | 4
5398 | energy log this day 02h |  |  | float | 3 | 2 | 4
5406 | energy log this day 03h |  |  | float | 3 | 2 | 4
5414 | energy log this day 04h |  |  | float | 3 | 2 | 4
5422 | energy log this day 05h |  |  | float | 3 | 2 | 4
5430 | energy log this day 06h |  |  | float | 3 | 2 | 4
5438 | energy log this day 07h |  |  | float | 3 | 2 | 4
5446 | energy log this day 08h |  |  | float | 3 | 2 | 4
5454 | energy log this day 09h |  |  | float | 3 | 2 | 4
5462 | energy log this day 10h |  |  | float | 3 | 2 | 4
5470 | energy log this day 11h |  |  | float | 3 | 2 | 4
5478 | energy log this day 12h |  |  | float | 3 | 2 | 4
5486 | energy log this day 13h |  |  | float | 3 | 2 | 4
5494 | energy log this day 14h |  |  | float | 3 | 2 | 4 | 전일 디멘트 로그
5502 | energy log this day 15h |  |  | float | 3 | 2 | 4
5510 | energy log this day 16h |  |  | float | 3 | 2 | 4
5518 | energy log this day 17h |  |  | float | 3 | 2 | 4
5526 | energy log this day 18h |  |  | float | 3 | 2 | 4
5534 | energy log this day 19h |  |  | float | 3 | 2 | 4
5542 | energy log this day 20h |  |  | float | 3 | 2 | 4
5550 | energy log this day 21h |  |  | float | 3 | 2 | 4
5558 | energy log this day 22h |  |  | float | 3 | 2 | 4
5566 | energy log this day 23h |  |  | float | 3 | 2 | 4
5574 |  |  |  | U16 | 3 | 1 | 6
demand log last day
5580 | Time Stamp |  |  | U32 | 3 | 2 | 1
5582 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
5774 |  |  |  | U16 | 3 | 1 | 6
ITIC
5780 | fr |  |  | U16 | 3 | 1 | 1
5781 | re |  |  | U16 | 3 | 1 | 1
5782 | count |  |  | U16 | 3 | 1 | 1
5783 | SEQ |  |  | U16 | 3 | 1 | 1
5784 | Log #1 | start ts |  | UTC | 3 | 2 | 1
5786 |  | start ts(ms) |  | U16 | 3 | 1 | 1
5787 |  | duration |  | U16 | 3 | 1 | 1
5788 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
5789 |  | mask |  | U16 | 3 | 1 | 1
5790 |  | Level 1 |  | float | 3 | 2 | 1
5792 |  | Level 2 |  | float | 3 | 2 | 1
5794 |  | Level 3 |  | float | 3 | 2 | 1
5796 |  | Normal |  | float | 3 | 2 | 1
5798 | Log #2 |  |  | U16 | 3 | 1 | 14
5812 | Log #3 |  |  | U16 | 3 | 1 | 14
5826 | Log #4 |  |  | U16 | 3 | 1 | 14
5840 | Log #5 |  |  | U16 | 3 | 1 | 14
5854 | Log #6 |  |  | U16 | 3 | 1 | 14
5868 | Log #7 |  |  | U16 | 3 | 1 | 14
5882 | Log #8 |  |  | U16 | 3 | 1 | 14
5896 | Log #9 |  |  | U16 | 3 | 1 | 14
5910 | Log #10 |  |  | U16 | 3 | 1 | 14
5924 | Log #11 |  |  | U16 | 3 | 1 | 14
5938 | Log #12 |  |  | U16 | 3 | 1 | 14
5952 | Log #13 |  |  | U16 | 3 | 1 | 14
5966 | Log #14 |  |  | U16 | 3 | 1 | 14
5980 | Log #15 |  |  | U16 | 3 | 1 | 14
5994 | Log #16 |  |  | U16 | 3 | 1 | 14
6008 | Log #17 |  |  | U16 | 3 | 1 | 14
6022 | Log #18 |  |  | U16 | 3 | 1 | 14
6036 | Log #19 |  |  | U16 | 3 | 1 | 14
6050 | Log #20 |  |  | U16 | 3 | 1 | 14
6064 | Log #21 |  |  | U16 | 3 | 1 | 14
6078 | Log #22 |  |  | U16 | 3 | 1 | 14
6092 | Log #23 |  |  | U16 | 3 | 1 | 14
6106 | Log #24 |  |  | U16 | 3 | 1 | 14
6120 | Log #25 |  |  | U16 | 3 | 1 | 14
6134 | Log #26 |  |  | U16 | 3 | 1 | 14
6148 | Log #27 |  |  | U16 | 3 | 1 | 14
6162 | Log #28 |  |  | U16 | 3 | 1 | 14
6176 | Log #29 |  |  | U16 | 3 | 1 | 14
6190 | Log #30 |  |  | U16 | 3 | 1 | 14
6204 | Log #31 |  |  | U16 | 3 | 1 | 14
6218 | Log #32 |  |  | U16 | 3 | 1 | 14
6232 |  |  |  | U16 | 3 | 1 | 8
ITIC(Configurator)
6240 | fr |  |  | U16 | 3 | 1 | 1
6241 | re |  |  | U16 | 3 | 1 | 1
6242 | count |  |  | U16 | 3 | 1 | 1
6243 | reserved |  |  | U16 | 3 | 1 | 1
6244 | Log #1 | start ts |  | UTC | 3 | 2 | 1
6246 |  | start ts(ms) |  | U16 | 3 | 1 | 1
6247 |  | duration |  | U16 | 3 | 1 | 1
6248 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
6249 |  | mask |  | U16 | 3 | 1 | 1
6250 |  | Level 1 |  | float | 3 | 2 | 1
6252 |  | Level 2 |  | float | 3 | 2 | 1
6254 |  | Level 3 |  | float | 3 | 2 | 1
6256 |  | Normal |  | float | 3 | 2 | 1
6258 | Log #2 |  |  | U16 | 3 | 1 | 14
6272 | Log #3 |  |  | U16 | 3 | 1 | 14
6286 | Log #4 |  |  | U16 | 3 | 1 | 14
6300 | Log #5 |  |  | U16 | 3 | 1 | 14
6314 | Log #6 |  |  | U16 | 3 | 1 | 14
6328 | Log #7 |  |  | U16 | 3 | 1 | 14
6342 | Log #8 |  |  | U16 | 3 | 1 | 14
6356 | Log #9 |  |  | U16 | 3 | 1 | 14
6370 | Log #10 |  |  | U16 | 3 | 1 | 14
6384 | Log #11 |  |  | U16 | 3 | 1 | 14
6398 | Log #12 |  |  | U16 | 3 | 1 | 14
6412 | Log #13 |  |  | U16 | 3 | 1 | 14
6426 | Log #14 |  |  | U16 | 3 | 1 | 14
6440 | Log #15 |  |  | U16 | 3 | 1 | 14
6454 | Log #16 |  |  | U16 | 3 | 1 | 14
6468 | Log #17 |  |  | U16 | 3 | 1 | 14
6482 | Log #18 |  |  | U16 | 3 | 1 | 14
6496 | Log #19 |  |  | U16 | 3 | 1 | 14
6510 | Log #20 |  |  | U16 | 3 | 1 | 14
6524 | Log #21 |  |  | U16 | 3 | 1 | 14
6538 | Log #22 |  |  | U16 | 3 | 1 | 14
6552 | Log #23 |  |  | U16 | 3 | 1 | 14
6566 | Log #24 |  |  | U16 | 3 | 1 | 14
6580 | Log #25 |  |  | U16 | 3 | 1 | 14
6594 | Log #26 |  |  | U16 | 3 | 1 | 14
6608 | Log #27 |  |  | U16 | 3 | 1 | 14
6622 | Log #28 |  |  | U16 | 3 | 1 | 14
6636 | Log #29 |  |  | U16 | 3 | 1 | 14
6650 | Log #30 |  |  | U16 | 3 | 1 | 14
6664 | Log #31 |  |  | U16 | 3 | 1 | 14
6678 | Log #32 |  |  | U16 | 3 | 1 | 14
6692 |  |  |  | U16 | 3 | 1 | 8
Setting 영역 시작
PQ Event
6700 | OC Level | 정격의 2배 |  | U16 | 3,16 | 1 | 1
6701 | OC Cycle | unused |  | U16 | 3,16 | 1 | 1
6702 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
6703 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
6704 |  |  |  | U16 | 3,16 | 1 | 2
6706 | Sag Level(%), 90% | < 90% |  | U16 | 3,16 | 1 | 1
6707 | Sag Cycle | unused |  | U16 | 3,16 | 1 | 1
6708 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
6709 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
6710 |  |  |  | U16 | 3,16 | 1 | 2
6712 | Swell Level(%), 110~200~ | > 110% |  | U16 | 3,16 | 1 | 1
6713 | Swell Cycle | unused |  | U16 | 3,16 | 1 | 1
6714 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
6715 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
6716 |  |  |  | U16 | 3,16 | 1 | 2
6718 | Interruption Level, 5% | < 5% |  | U16 | 3,16 | 1 | 1
6719 | Interruption Time, 60s | unused |  | U16 | 3,16 | 1 | 1
6720 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
6721 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
6722 |  |  |  | U16 | 3,16 | 1 | 2
Transient Trigger
6724 | Transient Voltage, HoldOff Time, 20ms | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
6725 | Transient Voltage, Absolute Peak Level, 200% | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
6726 | Transient Voltage, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
6727 | Transient Voltage, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
6728 | Transient Current, HoldOff Time | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
6729 | Transient Current, Absolute Peak Level | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
6730 | Transient Current, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
6731 | Transient Current, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
6732 |  |  |  | U16 | 3,16 | 1 | 12
Recorder
Waveform
6744 | Recorder resolution(32k, 8k) |  |  | U16 | 3,16 | 1 | 1
6745 | Recorded paramater (U or I) |  |  | U16 | 3,16 | 1 | 1
6746 | pre trigger time(0.1s) |  |  | U16 | 3,16 | 1 | 1
6747 | post trigger time(1s) |  |  | U16 | 3,16 | 1 | 1
Disturbance
6748 | Recorder resolution (Half Cycle) |  |  | U16 | 3,16 | 1 | 1
6749 | Recorded parametrs(U or I) |  |  | U16 | 3,16 | 1 | 1
6750 | pre trigger time(100 sample) |  |  | U16 | 3,16 | 1 | 1
6751 | post trigger time(900 sample) |  |  | U16 | 3,16 | 1 | 1
6752 |  |  |  | U16 | 3,16 | 1 | 12
Trend Recorder
6764 | Trend Group #1 Active |  |  | U16 | 3,16 | 1 | 1
6765 | Trend Group #1 Storage Interval |  |  | U16 | 3,16 | 1 | 1
6766 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
6767 | Trend Group #1, Channel #1 |  |  | U16 | 3,16 | 1 | 1
6768 | Trend Group #1, Channel #2 |  |  | U16 | 3,16 | 1 | 1
6769 | Trend Group #1, Channel #3 |  |  | U16 | 3,16 | 1 | 1
6770 | Trend Group #1, Channel #4 |  |  | U16 | 3,16 | 1 | 1
6771 | Trend Group #1, Channel #5 |  |  | U16 | 3,16 | 1 | 1
6772 | Trend Group #1, Channel #6 |  |  | U16 | 3,16 | 1 | 1
6773 | Trend Group #1, Channel #7 |  |  | U16 | 3,16 | 1 | 1
6774 | Trend Group #1, Channel #8 |  |  | U16 | 3,16 | 1 | 1
6775 | Trend Group #1, Channel #9 |  |  | U16 | 3,16 | 1 | 1
6776 | Trend Group #1, Channel #10 |  |  | U16 | 3,16 | 1 | 1
6777 | Trend Group #1, Channel #11 |  |  | U16 | 3,16 | 1 | 1
6778 | Trend Group #1, Channel #12 |  |  | U16 | 3,16 | 1 | 1
6779 | Trend Group #1, Channel #13 |  |  | U16 | 3,16 | 1 | 1
6780 | Trend Group #1, Channel #14 |  |  | U16 | 3,16 | 1 | 1
6781 | Trend Group #1, Channel #15 |  |  | U16 | 3,16 | 1 | 1
6782 | Trend Group #1, Channel #16 |  |  | U16 | 3,16 | 1 | 1
6783 | Trend Group #2 Active |  |  | U16 | 3,16 | 1 | 1
6784 | Trend Group #2 Storage Interval |  |  | U16 | 3,16 | 1 | 1
6785 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
6786 | Trend Group #2, Channel #1 |  |  | U16 | 3,16 | 1 | 1
6787 | Trend Group #2, Channel #2 |  |  | U16 | 3,16 | 1 | 1
6788 | Trend Group #2, Channel #3 |  |  | U16 | 3,16 | 1 | 1
6789 | Trend Group #2, Channel #4 |  |  | U16 | 3,16 | 1 | 1
6790 | Trend Group #2, Channel #5 |  |  | U16 | 3,16 | 1 | 1
6791 | Trend Group #2, Channel #6 |  |  | U16 | 3,16 | 1 | 1
6792 | Trend Group #2, Channel #7 |  |  | U16 | 3,16 | 1 | 1
6793 | Trend Group #2, Channel #8 |  |  | U16 | 3,16 | 1 | 1
6794 | Trend Group #2, Channel #9 |  |  | U16 | 3,16 | 1 | 1
6795 | Trend Group #2, Channel #10 |  |  | U16 | 3,16 | 1 | 1
6796 | Trend Group #2, Channel #11 |  |  | U16 | 3,16 | 1 | 1
6797 | Trend Group #2, Channel #12 |  |  | U16 | 3,16 | 1 | 1
6798 | Trend Group #2, Channel #13 |  |  | U16 | 3,16 | 1 | 1
6799 | Trend Group #2, Channel #14 |  |  | U16 | 3,16 | 1 | 1
6800 | Trend Group #2, Channel #15 |  |  | U16 | 3,16 | 1 | 1
6801 | Trend Group #2, Channel #16 |  |  | U16 | 3,16 | 1 | 1
6802 | Trend Group #3 Active |  |  | U16 | 3,16 | 1 | 1
6803 | Trend Group #3 Storage Interval |  |  | U16 | 3,16 | 1 | 1
6804 |  |  |  | U16 | 3,16 | 1 | 1
6805 | Trend Group #3, Channel #1 |  |  | U16 | 3,16 | 1 | 1
6806 | Trend Group #3, Channel #2 |  |  | U16 | 3,16 | 1 | 1
6807 | Trend Group #3, Channel #3 |  |  | U16 | 3,16 | 1 | 1
6808 | Trend Group #3, Channel #4 |  |  | U16 | 3,16 | 1 | 1
6809 | Trend Group #3, Channel #5 |  |  | U16 | 3,16 | 1 | 1
6810 | Trend Group #3, Channel #6 |  |  | U16 | 3,16 | 1 | 1
6811 | Trend Group #3, Channel #7 |  |  | U16 | 3,16 | 1 | 1
6812 | Trend Group #3, Channel #8 |  |  | U16 | 3,16 | 1 | 1
6813 | Trend Group #3, Channel #9 |  |  | U16 | 3,16 | 1 | 1
6814 | Trend Group #3, Channel #10 |  |  | U16 | 3,16 | 1 | 1
6815 | Trend Group #3, Channel #11 |  |  | U16 | 3,16 | 1 | 1
6816 | Trend Group #3, Channel #12 |  |  | U16 | 3,16 | 1 | 1
6817 | Trend Group #3, Channel #13 |  |  | U16 | 3,16 | 1 | 1
6818 | Trend Group #3, Channel #14 |  |  | U16 | 3,16 | 1 | 1
6819 | Trend Group #3, Channel #15 |  |  | U16 | 3,16 | 1 | 1
6820 | Trend Group #3, Channel #16 |  |  | U16 | 3,16 | 1 | 1
6821 | Trend Group #4 Active |  |  | U16 | 3,16 | 1 | 1
6822 | Trend Group #4 Storage Interval |  |  | U16 | 3,16 | 1 | 1
6823 |  |  |  | U16 | 3,16 | 1 | 1
6824 | Trend Group #4, Channel #1 |  |  | U16 | 3,16 | 1 | 1
6825 | Trend Group #4, Channel #2 |  |  | U16 | 3,16 | 1 | 1
6826 | Trend Group #4, Channel #3 |  |  | U16 | 3,16 | 1 | 1
6827 | Trend Group #4, Channel #4 |  |  | U16 | 3,16 | 1 | 1
6828 | Trend Group #4, Channel #5 |  |  | U16 | 3,16 | 1 | 1
6829 | Trend Group #4, Channel #6 |  |  | U16 | 3,16 | 1 | 1
6830 | Trend Group #4, Channel #7 |  |  | U16 | 3,16 | 1 | 1
6831 | Trend Group #4, Channel #8 |  |  | U16 | 3,16 | 1 | 1
6832 | Trend Group #4, Channel #9 |  |  | U16 | 3,16 | 1 | 1
6833 | Trend Group #4, Channel #10 |  |  | U16 | 3,16 | 1 | 1
6834 | Trend Group #4, Channel #11 |  |  | U16 | 3,16 | 1 | 1
6835 | Trend Group #4, Channel #12 |  |  | U16 | 3,16 | 1 | 1
6836 | Trend Group #4, Channel #13 |  |  | U16 | 3,16 | 1 | 1
6837 | Trend Group #4, Channel #14 |  |  | U16 | 3,16 | 1 | 1
6838 | Trend Group #4, Channel #15 |  |  | U16 | 3,16 | 1 | 1
6839 | Trend Group #4, Channel #16 |  |  | U16 | 3,16 | 1 | 1
6840 |  |  |  | U16 | 3,16 | 1 | 4
Power Quality Report
6844 | Active |  |  | U16 | 3,16 | 1 | 1
6845 | Start Day |  |  | U16 | 3,16 | 1 | 1
6846 |  |  |  | U16 |  | 1 | 8
Alarm Definition
6854 | compare Time Delay(1s) |  |  | U16 | 3,16 | 1 | 1
6855 |  |  |  | U16 |  | 1 | 1
6856 |  |  |  | U16 |  | 1 | 1
6857 |  |  |  | U16 |  | 1 | 1
Alarm Settings
6858 | Alarm Info #1 Channel(0:disabled, >0: enabled) |  |  | U16 | 3,16 | 1 | 1
6859 | Alarm Cond (0: < , 1:>) |  |  | U16 | 3,16 | 1 | 1
6860 | Hysteresis (% of Nominal) |  |  | U16 | 3,16 | 1 | 1
6861 | Alarm Action (None, Relay or Beep) |  |  | U16 | 3,16 | 1 | 1
6862 | Alarm Level |  |  | float | 3,16 | 2 | 1
6864 | Alarm Settings #2 |  |  | U16 | 3,16 | 1 | 6
6870 | Alarm Settings #3 |  |  | U16 | 3,16 | 1 | 6
6876 | Alarm Settings #4 |  |  | U16 | 3,16 | 1 | 6
6882 | Alarm Settings #5 |  |  | U16 | 3,16 | 1 | 6
6888 | Alarm Settings #6 |  |  | U16 | 3,16 | 1 | 6
6894 | Alarm Settings #7 |  |  | U16 | 3,16 | 1 | 6
6900 | Alarm Settings #8 |  |  | U16 | 3,16 | 1 | 6
6906 | Alarm Settings #9 |  |  | U16 | 3,16 | 1 | 6
6912 | Alarm Settings #10 |  |  | U16 | 3,16 | 1 | 6
6918 | Alarm Settings #11 |  |  | U16 | 3,16 | 1 | 6
6924 | Alarm Settings #12 |  |  | U16 | 3,16 | 1 | 6
6930 | Alarm Settings #13 |  |  | U16 | 3,16 | 1 | 6
6936 | Alarm Settings #14 |  |  | U16 | 3,16 | 1 | 6
6942 | Alarm Settings #15 |  |  | U16 | 3,16 | 1 | 6
6948 | Alarm Settings #16 |  |  | U16 | 3,16 | 1 | 6
6954 | Alarm Settings #17 |  |  | U16 | 3,16 | 1 | 6
6960 | Alarm Settings #18 |  |  | U16 | 3,16 | 1 | 6
6966 | Alarm Settings #19 |  |  | U16 | 3,16 | 1 | 6
6972 | Alarm Settings #20 |  |  | U16 | 3,16 | 1 | 6
6978 | Alarm Settings #21 |  |  | U16 | 3,16 | 1 | 6
6984 | Alarm Settings #22 |  |  | U16 | 3,16 | 1 | 6
6990 | Alarm Settings #23 |  |  | U16 | 3,16 | 1 | 6
6996 | Alarm Settings #24 |  |  | U16 | 3,16 | 1 | 6
7002 | Alarm Settings #25 |  |  | U16 | 3,16 | 1 | 6
7008 | Alarm Settings #26 |  |  | U16 | 3,16 | 1 | 6
7014 | Alarm Settings #27 |  |  | U16 | 3,16 | 1 | 6
7020 | Alarm Settings #28 |  |  | U16 | 3,16 | 1 | 6
7026 | Alarm Settings #29 |  |  | U16 | 3,16 | 1 | 6
7032 | Alarm Settings #30 |  |  | U16 | 3,16 | 1 | 6
7038 | Alarm Settings #31 |  |  | U16 | 3,16 | 1 | 6
7044 | Alarm Settings #32 |  |  | U16 | 3,16 | 1 | 6
7050

## #2CH modbus
address | name | 설명 | Unit | TYPE | FC | Word Count | Item Count
Metering
10000 | Time Stamp |  |  | UTC | 3 | 2 | 1
10002 | TYPE |  |  | U16 | 3 | 1 | 1
10003 | STATUS | 1 : online, 0 : offline |  | U16 | 3 | 1 | 1
10004 | Frequency | 라인주파수 | Hz | float | 3 | 2 | 1
10006 | Internal Temp |  | ℃ | float | 3 | 2 | 1
10008 | U1 | 상전압 1 | V | float | 3 | 2 | 1
10010 | U2 | 상전압 2 |  | float | 3 | 2 | 1
10012 | U3 | 상전압 3 |  | float | 3 | 2 | 1
10014 | U~ | 상전압 평균 |  | float | 3 | 2 | 1
10016 | U12 | 선간 전압 12 |  | float | 3 | 2 | 1
10018 | U23 | 선간 전압 23 |  | float | 3 | 2 | 1
10020 | U31 | 선간 전압 31 |  | float | 3 | 2 | 1
10022 | Upp~ | 선간 전압 평균 |  | float | 3 | 2 | 1
10024 | Uunbalance2 |  | % | float | 3 | 2 | 1 | Uu=neg/pos*100
10026 | Uunbalance0 |  |  | float | 3 | 2 | 1 | Uo=zero/pos*100
10028 | U Zero Sequence Mag. |  |  | float | 3 | 2 | 1
10030 | U Zero Sequence angle |  |  | float | 3 | 2 | 1
10032 | U Positive Sequence Mag. |  |  | float | 3 | 2 | 1
10034 | U Positive Sequence angle |  |  | float | 3 | 2 | 1
10036 | U Negative Sequence Mag |  |  | float | 3 | 2 | 1
10038 | U Negative Sequence angle |  |  | float | 3 | 2 | 1
10040 | Angle U1 |  |  | float | 3 | 2 | 1
10042 | Angle U2 |  |  | float | 3 | 2 | 1
10044 | Angle U3 |  |  | float | 3 | 2 | 1
10046 | U Underdeviation L1 |  | % | float | 3 | 2 | 1
10048 | U Underdeviation L2 |  | % | float | 3 | 2 | 1
10050 | U Underdeviation L3 |  | % | float | 3 | 2 | 1
10052 | U Overdeviation L1 |  | % | float | 3 | 2 | 1
10054 | U Overdeviation L2 |  | % | float | 3 | 2 | 1
10056 | U Overdeviation L3 |  | % | float | 3 | 2 | 1
10058 | I1 | 상전류 1 | A | float | 3 | 2 | 1
10060 | I2 | 상전류 2 |  | float | 3 | 2 | 1
10062 | I3 | 상전류 3 |  | float | 3 | 2 | 1
10064 | I~ |  |  | float | 3 | 2 | 1
10066 | I total (I1+I2+I3) |  |  | float | 3 | 2 | 1
10068 | In(Measured) |  |  | float | 3 | 2 | 1 | 1. 5A: -3P4W(In) -3P3W(Ig), 2. AT/VT: Ig로 사용
10070 | In(Calculated) | Ia+Ib+Ic+In = Ig |  | float | 3 | 2 | 1 | 1. 5A: -3P4W(Ig=Ia+Ib+Ic+In), -3P3W(Ig=Ia+Ib+Ic), 2. AT/VT: 5A와 동일
10072 | Ig |  |  | float | 3 | 2 | 1
10074 | I Zero Sequence Mag |  |  | float | 3 | 2 | 1
10076 | I Zero Sequence angle |  |  | float | 3 | 2 | 1
10078 | I Positive Sequence Mag. |  |  | float | 3 | 2 | 1
10080 | I Positive Sequence angle |  |  | float | 3 | 2 | 1
10082 | I Negative Sequence Mag. |  |  | float | 3 | 2 | 1
10084 | I Negative Sequence angle |  |  | float | 3 | 2 | 1
10086 | Angle I1 |  |  | float | 3 | 2 | 1
10088 | Angle I2 |  |  | float | 3 | 2 | 1
10090 | Angle I3 |  |  | float | 3 | 2 | 1
10092 | Iunbalance2 |  | % | float | 3 | 2 | 1
10094 | Iunbalance0 |  |  | float | 3 | 2 | 1
10096 | P1 | 유효전력 P1 | W | float | 3 | 2 | 1
10098 | P2 | 유효전력 P2 |  | float | 3 | 2 | 1
10100 | P3 | 유효전력 P3 |  | float | 3 | 2 | 1
10102 | P total | 유효전력 P-total |  | float | 3 | 2 | 1
10104 | fP1 |  |  | float | 3 | 2 | 1
10106 | fP2 |  |  | float | 3 | 2 | 1
10108 | fP3 |  |  | float | 3 | 2 | 1
10110 | fP total |  |  | float | 3 | 2 | 1
10112 | Q1 | 무효전력 Q1 | VAR | float | 3 | 2 | 1
10114 | Q2 | 무효전력 Q2 |  | float | 3 | 2 | 1
10116 | Q3 | 무효전력 Q3 |  | float | 3 | 2 | 1
10118 | Q total | 무효전력 Q-total |  | float | 3 | 2 | 1
10120 | fQ1 |  |  | float | 3 | 2 | 1
10122 | fQ2 |  |  | float | 3 | 2 | 1
10124 | fQ3 |  |  | float | 3 | 2 | 1
10126 | fQ total |  |  | float | 3 | 2 | 1
10128 | S1 | 피상전력 S1 | VA | float | 3 | 2 | 1
10130 | S2 | 피상전력 S2 |  | float | 3 | 2 | 1
10132 | S3 | 피상전력 S3 |  | float | 3 | 2 | 1
10134 | S total | 피상전력 S-total |  | float | 3 | 2 | 1
10136 | fS1 |  |  | float | 3 | 2 | 1
10138 | fS2 |  |  | float | 3 | 2 | 1
10140 | fS3 |  |  | float | 3 | 2 | 1
10142 | fS total |  |  | float | 3 | 2 | 1
10144 | PF1 | 역률 PF1 | % | float | 3 | 2 | 1
10146 | PF2 | 역률 PF2 |  | float | 3 | 2 | 1
10148 | PF3 | 역률 PF3 |  | float | 3 | 2 | 1
10150 | PF total | 역률 PF-total |  | float | 3 | 2 | 1
10152 | dPF1 |  | % | float | 3 | 2 | 1
10154 | dPF2 |  |  | float | 3 | 2 | 1
10156 | dPF3 |  |  | float | 3 | 2 | 1
10158 | dPF total |  |  | float | 3 | 2 | 1
10160 | deformed Power D L1 |  | W | float | 3 | 2 | 1 | S=sqrt {P^{2}+Q^{2}+D^{2}}
10162 | deformed Power D L2 |  |  | float | 3 | 2 | 1
10164 | deformed Power D L3 |  |  | float | 3 | 2 | 1
10166 | deformed Power D Total |  |  | float | 3 | 2 | 1
10168 | Power Angle(atan(fPt,fQt) L1 |  | Degree | float | 3 | 2 | 1 | Angle between fundamental phase voltage and phase current
10170 | Power Angle(atan(fPt,fQt) L2 |  |  | float | 3 | 2 | 1
10172 | Power Angle(atan(fPt,fQt) L3 |  |  | float | 3 | 2 | 1
10174 |  |  |  | float | 3 | 2 | 1
10176 | THD V1 |  | % | float | 3 | 2 | 1
10178 | THD V2 |  |  | float | 3 | 2 | 1 | Chip에서 제공하는 결과 사용
10180 | THD V3 |  |  | float | 3 | 2 | 1
10182 | THD V12 |  |  | float | 3 | 2 | 1
10184 | THD V23 |  |  | float | 3 | 2 | 1
10186 | THD V31 |  |  | float | 3 | 2 | 1
10188 | CF V1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
10190 | CF V2 |  |  | float | 3 | 2 | 1
10192 | CF V3 |  |  | float | 3 | 2 | 1
10194 | CF V12 |  |  | float | 3 | 2 | 1
10196 | CF V23 |  |  | float | 3 | 2 | 1
10198 | CF V31 |  |  | float | 3 | 2 | 1
10200 | THD I1 |  |  | float | 3 | 2 | 1
10202 | THD I2 |  |  | float | 3 | 2 | 1
10204 | THD I3 |  |  | float | 3 | 2 | 1
10206 | TDD I1 |  |  | float | 3 | 2 | 1
10208 | TDD I2 |  |  | float | 3 | 2 | 1
10210 | TDD I3 |  |  | float | 3 | 2 | 1
10212 | K I1 | K-FACTOR : 고조파 허용율 |  | float | 3 | 2 | 1
10214 | K I2 |  |  | float | 3 | 2 | 1
10216 | K I3 |  |  | float | 3 | 2 | 1
10218 | CF I1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
10220 | CF I2 |  |  | float | 3 | 2 | 1
10222 | CF I3 |  |  | float | 3 | 2 | 1
10224 | fU1 | 기본파 U1 | V | float | 3 | 2 | 1
10226 | fU2 | 기본파 U2 |  | float | 3 | 2 | 1
10228 | fU3 | 기본파 U3 |  | float | 3 | 2 | 1
10230 | fU~ | 기본파 전압 평균 |  | float | 3 | 2 | 1
10232 | fI1 | 기본파 I1 | A | float | 3 | 2 | 1
10234 | fI2 | 기본파 I2 |  | float | 3 | 2 | 1
10236 | fI3 | 기본파 I3 |  | float | 3 | 2 | 1
10238 | fI~ | 기본파 전류 평균 |  | float | 3 | 2 | 1
Energy
10240 | import kwh(0 ~ 999,999,999.9 kw) TOTAL | 누적 TOTAL 유효전력량 |  | U32 | 3 | 2 | 1
10242 | export kwh TOTAL |  |  | U32 | 3 | 2 | 1
10244 | import kvarh TOTAL |  |  | U32 | 3 | 2 | 1
10246 | export kvarh TOTAL |  |  | U32 | 3 | 2 | 1
10248 | kvah TOTAL |  |  | U32 | 3 | 2 | 1
10250 |  |  |  | U32 | 3 | 2 | 1
10252 | import kwh(0 ~ 999,999,999.9 kw) L1 | 누적 L1 유효전력량 |  | U32 | 3 | 2 | 1
10254 | export kwh L1 |  |  | U32 | 3 | 2 | 1
10256 | import kvarh L1 |  |  | U32 | 3 | 2 | 1
10258 | export kvarh L1 |  |  | U32 | 3 | 2 | 1
10260 | kvah L1 |  |  | U32 | 3 | 2 | 1
10262 |  |  |  | U32 | 3 | 2 | 1
10264 | import kwh(0 ~ 999,999,999.9 kw) L2 | 누적 L2 유효전력량 |  | U32 | 3 | 2 | 1
10266 | export kwh L2 |  |  | U32 | 3 | 2 | 1
10268 | import kvarh L2 |  |  | U32 | 3 | 2 | 1
10270 | export kvarh L2 |  |  | U32 | 3 | 2 | 1
10272 | kvah L2 |  |  | U32 | 3 | 2 | 1
10274 |  |  |  | U32 | 3 | 2 | 1
10276 | import kwh(0 ~ 999,999,999.9 kw) L3 | 누적 L3 유효전력량 |  | U32 | 3 | 2 | 1
10278 | export kwh L3 |  |  | U32 | 3 | 2 | 1
10280 | import kvarh L3 |  |  | U32 | 3 | 2 | 1
10282 | export kvarh L3 |  |  | U32 | 3 | 2 | 1
10284 | kvah L3 |  |  | U32 | 3 | 2 | 1
10286 |  |  |  | U32 | 3 | 2 | 1
10288 | import kwh this month TOTAL | TOTAL THIS MONTH |  | U32 | 3 | 2 | 1
10290 | export kwh this month TOTAL |  |  | U32 | 3 | 2 | 1
10292 | import kvarh this month TOTAL |  |  | U32 | 3 | 2 | 1
10294 | export kvarh this month TOTAL |  |  | U32 | 3 | 2 | 1
10296 | kvah this month TOTAL |  |  | U32 | 3 | 2 | 1
10298 |  |  |  | U32 | 3 | 2 | 1
10300 | import kwh this month L1 | L1 THIS MONTH |  | U32 | 3 | 2 | 1
10302 | export kwh this month L1 |  |  | U32 | 3 | 2 | 1
10304 | import kvarh this month L1 |  |  | U32 | 3 | 2 | 1
10306 | export kvarh this month L1 |  |  | U32 | 3 | 2 | 1
10308 | kvah this month L1 |  |  | U32 | 3 | 2 | 1
10310 |  |  |  | U32 | 3 | 2 | 1
10312 | import kwh this month L2 | L2 THIS MONTH |  | U32 | 3 | 2 | 1
10314 | export kwh this month L2 |  |  | U32 | 3 | 2 | 1
10316 | import kvarh this month L2 |  |  | U32 | 3 | 2 | 1
10318 | export kvarh this month L2 |  |  | U32 | 3 | 2 | 1
10320 | kvah this month L2 |  |  | U32 | 3 | 2 | 1
10322 |  |  |  | U32 | 3 | 2 | 1
10324 | import kwh this month L3 | L3 THIS MONTH |  | U32 | 3 | 2 | 1
10326 | export kwh this month L3 |  |  | U32 | 3 | 2 | 1
10328 | import kvarh this month L3 |  |  | U32 | 3 | 2 | 1
10330 | export kvarh this month L3 |  |  | U32 | 3 | 2 | 1
10332 | kvah this month L3 |  |  | U32 | 3 | 2 | 1
10334 |  |  |  | U32 | 3 | 2 | 1
10336 | import kwh last month TOTAL | TOTAL LAST MONTH |  | U32 | 3 | 2 | 1
10338 | export kwh last month |  |  | U32 | 3 | 2 | 1
10340 | import kvarh last month |  |  | U32 | 3 | 2 | 1
10342 | export kvarh last month |  |  | U32 | 3 | 2 | 1
10344 | kvah last month |  |  | U32 | 3 | 2 | 1
10346 |  |  |  | U32 | 3 | 2 | 1
10348 | import kwh last month L1 | L1 LAST MONTH |  | U32 | 3 | 2 | 1
10350 | export kwh last month |  |  | U32 | 3 | 2 | 1
10352 | import kvarh last month |  |  | U32 | 3 | 2 | 1
10354 | export kvarh last month |  |  | U32 | 3 | 2 | 1
10356 | kvah last month |  |  | U32 | 3 | 2 | 1
10358 |  |  |  | U32 | 3 | 2 | 1
10360 | import kwh last month L2 | L2 LAST MONTH |  | U32 | 3 | 2 | 1
10362 | export kwh last month |  |  | U32 | 3 | 2 | 1
10364 | import kvarh last month |  |  | U32 | 3 | 2 | 1
10366 | export kvarh last month |  |  | U32 | 3 | 2 | 1
10368 | kvah last month |  |  | U32 | 3 | 2 | 1
10370 |  |  |  | U32 | 3 | 2 | 1
10372 | import kwh last month L3 | L3 LAST MONTH |  | U32 | 3 | 2 | 1
10374 | export kwh last month |  |  | U32 | 3 | 2 | 1
10376 | import kvarh last month |  |  | U32 | 3 | 2 | 1
10378 | export kvarh last month |  |  | U32 | 3 | 2 | 1
10380 | kvah last month |  |  | U32 | 3 | 2 | 1
10382 |  |  |  | U32 | 3 | 2 | 1
10384 | import kwh | TOTAL,L1,L2,L3 |  | U64 | 3 | 4 | 4
10400 | export kwh |  |  | U64 | 3 | 4 | 4
10416 | import kvarh |  |  | U64 | 3 | 4 | 4
10432 | export kvarh |  |  | U64 | 3 | 4 | 4
10448 | kvah |  |  | U64 | 3 | 4 | 4
10464 |  |  |  | U64 | 3 | 4 | 4
Demand
10480 | Time Stamp |  |  | UTC | 3 | 2 | 1
10482 | Max Demand P(import) |  |  | float | 3 | 2 | 1
10484 | Time Stamp |  |  | UTC | 3 | 2 | 1
10486 | Max Demand P(export) |  |  | float | 3 | 2 | 1
10488 | Time Stamp |  |  | UTC | 3 | 2 | 1
10490 | Max Demand Q(import) |  |  | float | 3 | 2 | 1
10492 | Time Stamp |  |  | UTC | 3 | 2 | 1
10494 | Max Demand Q(export) |  |  | float | 3 | 2 | 1
10496 | Time Stamp |  |  | UTC | 3 | 2 | 1
10498 | Max Demand S |  |  | float | 3 | 2 | 1
10500 | Time Stamp |  |  | UTC | 3 | 2 | 1
10502 | Max Demand I1 |  |  | float | 3 | 2 | 1
10504 | Time Stamp |  |  | UTC | 3 | 2 | 1
10506 | Max Demand I2 |  |  | float | 3 | 2 | 1
10508 | Time Stamp |  |  | UTC | 3 | 2 | 1
10510 | Max Demand I3 |  |  | float | 3 | 2 | 1
10512 | Demand time stamp |  |  | UTC | 3 | 2 | 1
10514 | Demand P(import) |  |  | float | 3 | 2 | 1
10516 | Demand P(export) |  |  | float | 3 | 2 | 1 | 최근 24시간 그래프 그린다
10518 | Demand Q(import) |  |  | float | 3 | 2 | 1
10520 | Demand Q(export) |  |  | float | 3 | 2 | 1
10522 | Demand S(export) |  |  | float | 3 | 2 | 1
10524 | Demand I1 |  |  | float | 3 | 2 | 1
10526 | Demand I2 |  |  | float | 3 | 2 | 1
10528 | Demand I3 |  |  | float | 3 | 2 | 1
10530 | Present Demand P(import) |  |  | float | 3 | 2 | 1
10532 | Present Demand P(export) |  |  | float | 3 | 2 | 1
10534 | Present Demand Q(import) |  |  | float | 3 | 2 | 1
10536 | Present Demand Q(export) |  |  | float | 3 | 2 | 1
10538 | Present Demand S(export) |  |  | float | 3 | 2 | 1
10540 | Forecast Demand P(export) |  |  | float | 3 | 2 | 1
10542 | Demand P 15m(import) |  |  | float | 3 | 2 | 1
10544 |  |  |  | float | 3 | 2 | 1
10546 |  |  |  | float | 3 | 2 | 1
10548 | Time Stamp(Demand Log 시작일) |  |  | U32 | 3 | 2 | 1
10550 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
10742 |  |  |  | float | 3 | 2 | 19
Voltage Quality RealTime Value
10780 | Voltage Under Deviation L1 |  | % | float | 3 | 2 | 1
10782 | Voltage Under Deviation L2 |  | % | float | 3 | 2 | 1
10784 | Voltage Under Deviation L3 |  | % | float | 3 | 2 | 1
10786 | Voltage Under Value L1 |  | rms | float | 3 | 2 | 1
10788 | Voltage Under Value L2 |  | rms | float | 3 | 2 | 1
10790 | Voltage Under Value L3 |  | rms | float | 3 | 2 | 1
10792 | Voltage Over Deviation L1 |  | % | float | 3 | 2 | 1
10794 | Voltage Over Deviation L2 |  | % | float | 3 | 2 | 1
10796 | Voltage Over Deviation L3 |  | % | float | 3 | 2 | 1
10798 | Voltage Over Value L1 |  | rms | float | 3 | 2 | 1
10800 | Voltage Over Value L2 |  | rms | float | 3 | 2 | 1
10802 | Voltage Over Value L3 |  | rms | float | 3 | 2 | 1
10804 | Flickers Pi L1 | 150/180 Cycles |  | float | 3 | 2 | 1
10806 | Flickers Pi L2 |  |  | float | 3 | 2 | 1
10808 | Flickers Pi L3 |  |  | float | 3 | 2 | 1
10810 | Flicker Pst L1 | 10min |  | float | 3 | 2 | 1
10812 | Flicker Pst L2 |  |  | float | 3 | 2 | 1
10814 | Flicker Pst L3 |  |  | float | 3 | 2 | 1
10816 | Flicker Plt L1 | 2hr |  | float | 3 | 2 | 1 | 최근 24시간 그래프 그린다
10818 | Flicker Plt L2 |  |  | float | 3 | 2 | 1
10820 | Flicker Plt L3 |  |  | float | 3 | 2 | 1
10822 | Signaling Volt L1 | Magnitude of current 10/12 cycles as a percentage of nominal voltage. |  | float | 3 | 2 | 1
10824 | Signaling Volt L2 |  |  | float | 3 | 2 | 1
10826 | Signaling Volt L3 |  |  | float | 3 | 2 | 1
10828 | Signaling Volt Max L1 | Maximum magnitude of MSV from recording started as a percentage of nominal voltage |  | float | 3 | 2 | 1
10830 | Signaling Volt Max L2 |  |  | float | 3 | 2 | 1
10832 | Signaling Volt Max L3 |  |  | float | 3 | 2 | 1
10834 |  |  |  | float | 3 | 2 | 23
EN50160 This Week
10880 | start date |  |  | UTC | 3 | 2 | 1
10882 | end date |  |  | UTC | 3 | 2 | 1
10884 | status&compliance | bit 0: Freq Var1 bit 1: Freq Var2 bit 2: Volt Var1 L1 bit 3: Volt Var1 L2 bit 4: Volt Var1 L3 bit 5: Volt Var2 L1 bit 6: Volt Var2 L2 bit 7: Volt Var2 L3 bit 8: Unbalance bit 9: Volt THD L1 bit 10: Volt THD L2 bit 11: Volt THD L3 bit 12: Volt HD L1 bit 13: Volt HD L2 bit 14: Volt HD L3 bit 15: Pst L1 bit 16: Pst L2 bit 17: Pst L3 bit 18: Plt L1 bit 19: Plt L2 bit 20: Plt L3 bit 21: SigVolt L1 bit 22: SigVolt L2 bit 23: SigVolt L3 bit 31: Complete [status] 0: OK 1: failed |  | U32 | 3 | 2 | 1
10886 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1 | 95%/Week
10887 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1 | Info Only
10888 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
10889 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
10890 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
10891 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
10892 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
10893 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1 | Info Only
10894 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
10895 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
10896 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
10897 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
10898 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
10899 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
10900 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
10901 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
10902 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
10903 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
10904 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
10905 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
10906 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
10907 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
10908 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
10909 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
10910 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
10911 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1 | 99%/Day
10912 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
10913 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
10914 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
10915 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
10916 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
10917 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
10918 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
10919 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
10920 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
10921 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
10922 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
10923 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
10924 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
10925 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
10926 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
10927 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
10928 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
10929 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
EN50160 Last Week
10930 | start date |  |  | UTC | 3 | 2 | 1
10932 | end date |  |  | UTC | 3 | 2 | 1
10934 | status |  |  | U16 | 3 | 1 | 1
10935 | compilance |  |  | U16 | 3 | 1 | 1
10936 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1
10937 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1
10938 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
10939 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
10940 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1
10941 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
10942 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
10943 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1
10944 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
10945 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
10946 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1
10947 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
10948 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
10949 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1
10950 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
10951 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
10952 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1
10953 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
10954 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
10955 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1
10956 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
10957 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
10958 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1
10959 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
10960 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
10961 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1
10962 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
10963 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
10964 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
10965 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
10966 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
10967 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
10968 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
10969 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
10970 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
10971 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
10972 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
10973 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
10974 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
10975 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
10976 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
10977 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
10978 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
10979 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
Harmonics
10980 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
11044 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
11108 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
11172 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
11236 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
11300 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
11364 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
11428 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
11492 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
11556 |  |  |  | S16 | 3 | 1 | 24
Inter Harmonics
11580 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
11644 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
11708 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
11772 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
11836 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
11900 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
11964 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
12028 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
12092 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
12156 |  |  |  | S16 | 3 | 1 | 24
Max/Min
12180 | fr |  |  | U16 | 3 | 1 | 1
12181 | re |  |  | U16 | 3 | 1 | 1
12182 | Reset TimeStamp |  |  | UTC | 3 | 2 | 1
12184 | Frequency | Max |  | float | 3 | 2 | 1
12186 |  | Max Timestamp |  | UTC | 3 | 2 | 1
12188 |  | Min |  | float | 3 | 2 | 1
12190 |  | Min Timestamp |  | UTC | 3 | 2 | 1
12192 | Temp |  |  | float | 3 | 2 | 4
12200 | U1 |  |  | float | 3 | 2 | 4
12208 | U2 |  |  | float | 3 | 2 | 4
12216 | U3 |  |  | float | 3 | 2 | 4 | http://www.relaytech.com/symcomp_calculator.htm
12224 | U~ |  |  | float | 3 | 2 | 4
12232 | U12 |  |  | float | 3 | 2 | 4
12240 | U23 |  |  | float | 3 | 2 | 4
12248 | U31 |  |  | float | 3 | 2 | 4
12256 | Upp~ |  |  | float | 3 | 2 | 4
12264 | I1 |  |  | float | 3 | 2 | 4
12272 | I2 |  |  | float | 3 | 2 | 4
12280 | I3 |  |  | float | 3 | 2 | 4
12288 | I~ |  |  | float | 3 | 2 | 4
12296 | I total |  |  | float | 3 | 2 | 4
12304 | In |  |  | float | 3 | 2 | 4
12312 | Isum |  |  | float | 3 | 2 | 4
12320 | P1 |  |  | float | 3 | 2 | 4
12328 | P2 |  |  | float | 3 | 2 | 4
12336 | P3 |  |  | float | 3 | 2 | 4
12344 | P total |  |  | float | 3 | 2 | 4
12352 | Q1 |  |  | float | 3 | 2 | 4
12360 | Q2 |  |  | float | 3 | 2 | 4
12368 | Q3 |  |  | float | 3 | 2 | 4
12376 | Q total |  |  | float | 3 | 2 | 4
12384 | S1 |  |  | float | 3 | 2 | 4
12392 | S2 |  |  | float | 3 | 2 | 4
12400 | S3 |  |  | float | 3 | 2 | 4
12408 | S total |  |  | float | 3 | 2 | 4
12416 | PF L1 |  |  | float | 3 | 2 | 4
12424 | PF L2 |  |  | float | 3 | 2 | 4
12432 | PF L3 |  |  | float | 3 | 2 | 4
12440 | PF total |  |  | float | 3 | 2 | 4
12448 | THD U1 |  |  | float | 3 | 2 | 4
12456 | THD U2 |  |  | float | 3 | 2 | 4
12464 | THD U3 |  |  | float | 3 | 2 | 4
12472 | THD U12 |  |  | float | 3 | 2 | 4
12480 | THD U23 |  |  | float | 3 | 2 | 4
12488 | THD U31 |  |  | float | 3 | 2 | 4
12496 | THD I1 |  |  | float | 3 | 2 | 4
12504 | THD I2 |  |  | float | 3 | 2 | 4
12512 | THD I3 |  |  | float | 3 | 2 | 4
12520 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
12522 | reserved |  |  | U16 | 3 | 1 | 1
12523 | CRC |  |  | U16 | 3 | 1 | 1
12524 |  |  |  | U16 | 3 | 1 | 6
alarm status
12530 | fr |  |  | U16 | 3 | 1 | 1
12531 | re |  |  | U16 | 3 | 1 | 1
12532 | reset Ts |  |  | UTC | 3 | 2 | 1
12534 | Alarm State #1 | Alarm Channel |  | U16 | 3 | 1 | 1
12535 |  | Alarm Condition |  | U16 | 3 | 1 | 1
12536 |  | Alarm Level |  | float | 3 | 2 | 1
12538 |  | Alarm Status |  | U16 | 3 | 1 | 1
12539 |  | Alarm Count |  | U16 | 3 | 1 | 1
12540 | Alarm State #2 |  |  | U16 | 3 | 1 | 6
12546 | Alarm State #3 |  |  | U16 | 3 | 1 | 6
12552 | Alarm State #4 |  |  | U16 | 3 | 1 | 6
12558 | Alarm State #5 |  |  | U16 | 3 | 1 | 6
12564 | Alarm State #6 |  |  | U16 | 3 | 1 | 6
12570 | Alarm State #7 |  |  | U16 | 3 | 1 | 6
12576 | Alarm State #8 |  |  | U16 | 3 | 1 | 6
12582 | Alarm State #9 |  |  | U16 | 3 | 1 | 6
12588 | Alarm State #10 |  |  | U16 | 3 | 1 | 6
12594 | Alarm State #11 |  |  | U16 | 3 | 1 | 6
12600 | Alarm State #12 |  |  | U16 | 3 | 1 | 6
12606 | Alarm State #13 |  |  | U16 | 3 | 1 | 6
12612 | Alarm State #14 |  |  | U16 | 3 | 1 | 6
12618 | Alarm State #15 |  |  | U16 | 3 | 1 | 6
12624 | Alarm State #16 |  |  | U16 | 3 | 1 | 6
12630 | Alarm State #17 |  |  | U16 | 3 | 1 | 6
12636 | Alarm State #18 |  |  | U16 | 3 | 1 | 6
12642 | Alarm State #19 |  |  | U16 | 3 | 1 | 6
12648 | Alarm State #20 |  |  | U16 | 3 | 1 | 6
12654 | Alarm State #21 |  |  | U16 | 3 | 1 | 6
12660 | Alarm State #22 |  |  | U16 | 3 | 1 | 6
12666 | Alarm State #23 |  |  | U16 | 3 | 1 | 6
12672 | Alarm State #24 |  |  | U16 | 3 | 1 | 6
12678 | Alarm State #25 |  |  | U16 | 3 | 1 | 6
12684 | Alarm State #26 |  |  | U16 | 3 | 1 | 6
12690 | Alarm State #27 |  |  | U16 | 3 | 1 | 6
12696 | Alarm State #28 |  |  | U16 | 3 | 1 | 6
12702 | Alarm State #29 |  |  | U16 | 3 | 1 | 6
12708 | Alarm State #30 |  |  | U16 | 3 | 1 | 6
12714 | Alarm State #31 |  |  | U16 | 3 | 1 | 6
12720 | Alarm State #32 |  |  | U16 | 3 | 1 | 6
12726 | update Ts |  |  | U32 | 3 | 2 | 1
12728 | Global Alarm Status | (alarm 하나라도 있으면 1, 아니면 0) |  | U16 | 3 | 1 | 1
12729 |  |  |  | U16 | 3 | 1 | 1
alarm log
12730 | fr | 0 ~ 1023 |  | U16 | 3 | 1 | 1
12731 | re | 0 ~ 1023 |  | U16 | 3 | 1 | 1
12732 | count | 전체 log 수 |  | U16 | 3 | 1 | 1
12733 | seq |  |  | U16 | 3 | 1 | 1
12734 | Alarm Log #1 | Time Stamp |  | UTC | 3 | 2 | 1 | 2019-5-11변경
12736 |  | status |  | U16 | 3 | 1 | 1
12737 |  | Alarm Channel & Condition |  | U16 | 3 | 1 | 1
12738 |  | level |  | float | 3 | 2 | 1
12740 |  | Value |  | float | 3 | 2 | 1
12742 | Alarm Log #2 |  |  | U16 | 3 | 1 | 8
12750 | Alarm Log #3 |  |  | U16 | 3 | 1 | 8
12758 | Alarm Log #4 |  |  | U16 | 3 | 1 | 8
12766 | Alarm Log #5 |  |  | U16 | 3 | 1 | 8
12774 | Alarm Log #6 |  |  | U16 | 3 | 1 | 8
12782 | Alarm Log #7 |  |  | U16 | 3 | 1 | 8
12790 | Alarm Log #8 |  |  | U16 | 3 | 1 | 8
12798 | Alarm Log #9 |  |  | U16 | 3 | 1 | 8
12806 | Alarm Log #10 |  |  | U16 | 3 | 1 | 8
12814 | Alarm Log #11 |  |  | U16 | 3 | 1 | 8
12822 | Alarm Log #12 |  |  | U16 | 3 | 1 | 8
12830 | Alarm Log #13 |  |  | U16 | 3 | 1 | 8
12838 | Alarm Log #14 |  |  | U16 | 3 | 1 | 8
12846 | Alarm Log #15 |  |  | U16 | 3 | 1 | 8
12854 | Alarm Log #16 |  |  | U16 | 3 | 1 | 8
12862 | Alarm Log #17 |  |  | U16 | 3 | 1 | 8
12870 | Alarm Log #18 |  |  | U16 | 3 | 1 | 8
12878 | Alarm Log #19 |  |  | U16 | 3 | 1 | 8
12886 | Alarm Log #20 |  |  | U16 | 3 | 1 | 8
12894 | Alarm Log #21 |  |  | U16 | 3 | 1 | 8
12902 | Alarm Log #22 |  |  | U16 | 3 | 1 | 8
12910 | Alarm Log #23 |  |  | U16 | 3 | 1 | 8
12918 | Alarm Log #24 |  |  | U16 | 3 | 1 | 8
12926 | Alarm Log #25 |  |  | U16 | 3 | 1 | 8
12934 | Alarm Log #26 |  |  | U16 | 3 | 1 | 8
12942 | Alarm Log #27 |  |  | U16 | 3 | 1 | 8
12950 | Alarm Log #28 |  |  | U16 | 3 | 1 | 8
12958 | Alarm Log #29 |  |  | U16 | 3 | 1 | 8
12966 | Alarm Log #30 |  |  | U16 | 3 | 1 | 8
12974 | Alarm Log #31 |  |  | U16 | 3 | 1 | 8
12982 | Alarm Log #32 |  |  | U16 | 3 | 1 | 8
12990 |  |  |  | U16 | 3 | 1 | 40
이벤트 리스트
13030 | fr | 0 ~ 1023 |  | U16 | 3 | 1 | 1
13031 | re | 0 ~ 1023 |  | U16 | 3 | 1 | 1
13032 | count | 0 ~ 1023 |  | U16 | 3 | 1 | 1
13033 | seq |  |  | U16 | 3 | 1 | 1
PQ 이벤트(Sag, Swell, Transient, OC)
13034 | start ts |  |  | UTC | 3 | 2 | 1
13036 | start ts(ms) |  |  | U16 | 3 | 1 | 1
13037 | duration |  |  | U16 | 3 | 1 | 1
13038 | type | 1 : E_SAG 2 : E_SWELL 3 : E_sINTR 4 : E_lINTR 5 : E_OC 6 : E_RVC 7 : E_TrV 8 : E_TrC |  | U16 | 3 | 1 | 1
13039 | mask |  |  | U16 | 3 | 1 | 1
13040 | Level 1 |  |  | float | 3 | 2 | 1
13042 | Level 2 |  |  | float | 3 | 2 | 1
13044 | Level 3 |  |  | float | 3 | 2 | 1
13046 | PQ Event #2 |  |  | U16 | 3 | 1 | 12
13058 | PQ Event #3 |  |  | U16 | 3 | 1 | 12
13070 | PQ Event #4 |  |  | U16 | 3 | 1 | 12
13082 | PQ Event #5 |  |  | U16 | 3 | 1 | 12
13094 | PQ Event #6 |  |  | U16 | 3 | 1 | 12
13106 | PQ Event #7 |  |  | U16 | 3 | 1 | 12
13118 | PQ Event #8 |  |  | U16 | 3 | 1 | 12
13130 | PQ Event #9 |  |  | U16 | 3 | 1 | 12
13142 | PQ Event #10 |  |  | U16 | 3 | 1 | 12
13154 | PQ Event #11 |  |  | U16 | 3 | 1 | 12
13166 | PQ Event #12 |  |  | U16 | 3 | 1 | 12
13178 | PQ Event #13 |  |  | U16 | 3 | 1 | 12
13190 | PQ Event #14 |  |  | U16 | 3 | 1 | 12
13202 | PQ Event #15 |  |  | U16 | 3 | 1 | 12
13214 | PQ Event #16 |  |  | U16 | 3 | 1 | 12
13226 | PQ Event #17 |  |  | U16 | 3 | 1 | 12
13238 | PQ Event #18 |  |  | U16 | 3 | 1 | 12
13250 | PQ Event #19 |  |  | U16 | 3 | 1 | 12
13262 | PQ Event #20 |  |  | U16 | 3 | 1 | 12
13274 | PQ Event #21 |  |  | U16 | 3 | 1 | 12
13286 | PQ Event #22 |  |  | U16 | 3 | 1 | 12
13298 | PQ Event #23 |  |  | U16 | 3 | 1 | 12
13310 | PQ Event #24 |  |  | U16 | 3 | 1 | 12
13322 | PQ Event #25 |  |  | U16 | 3 | 1 | 12
13334 | PQ Event #26 |  |  | U16 | 3 | 1 | 12
13346 | PQ Event #27 |  |  | U16 | 3 | 1 | 12
13358 | PQ Event #28 |  |  | U16 | 3 | 1 | 12
13370 | PQ Event #29 |  |  | U16 | 3 | 1 | 12
13382 | PQ Event #30 |  |  | U16 | 3 | 1 | 12
13394 | PQ Event #31 |  |  | U16 | 3 | 1 | 12
13406 | PQ Event #32 |  |  | U16 | 3 | 1 | 12
13418 |  |  |  | U16 | 3 | 1 | 2
PQ Event Counter
13420 |  |  |  | U16 | 3 | 1 | 1
13421 |  |  |  | U16 | 3 | 1 | 1
13422 |  |  |  | U16 | 3 | 1 | 1
13423 | Sag Coount |  |  | U16 | 3 | 1 | 1
13424 | Swell Count |  |  | U16 | 3 | 1 | 1
13425 |  |  |  | U16 | 3 | 1 | 1
13426 |  |  |  | U16 | 3 | 1 | 1
13427 |  |  |  | U16 | 3 | 1 | 1
13428 |  |  |  | U16 | 3 | 1 | 1
13429 |  |  |  | U16 | 3 | 1 | 1
Wave Sample | [7 empty] | 32K: 67,107,786 8K: 74,518,668 첫번째 번지 접근시 wave data를 modbus map으로 load 한다
13430 | Wave Form V1 (160 sample) |  |  | S16 | 3 | 1 | 160
13590 | Wave Form V2 (160 sample) |  |  | S16 | 3 | 1 | 160
13750 | Wave Form V3 (160 sample) |  |  | S16 | 3 | 1 | 160
13910 | Wave Form V12 (160 sample) |  |  | S16 | 3 | 1 | 160
14070 | Wave Form V23 (160 sample) |  |  | S16 | 3 | 1 | 160
14230 | Wave Form V31 (160 sample) |  |  | S16 | 3 | 1 | 160
14390 | Wave Form I1 (160 sample) |  |  | S16 | 3 | 1 | 160
14550 | Wave Form I2 (160 sample) |  |  | S16 | 3 | 1 | 160
14710 | Wave Form I3 (160 sample) |  |  | S16 | 3 | 1 | 160
14870 | vscale |  |  | float | 3 | 2 | 1
14872 | iscale |  |  | float | 3 | 2 | 1
14874 |  |  |  | S16 | 3 | 1 | 6
월간리포트 생성위한 10분 평균
14880 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
14882 | U1 |  |  | float | 3 | 2 | 1
14884 | U2 |  |  | float | 3 | 2 | 1
14886 | U3 |  |  | float | 3 | 2 | 1
14888 | U THD1 |  |  | float | 3 | 2 | 1
14890 | U THD2 |  |  | float | 3 | 2 | 1
14892 | U THD3 |  |  | float | 3 | 2 | 1
14894 | Upp THD1 |  |  | float | 3 | 2 | 1
14896 | Upp THD2 |  |  | float | 3 | 2 | 1
14898 | Upp THD3 |  |  | float | 3 | 2 | 1
14900 | U Unbal Uu |  |  | float | 3 | 2 | 1
14902 | U Unbal Uo |  |  | float | 3 | 2 | 1
14904 | I1 |  |  | float | 3 | 2 | 1
14906 | I2 |  |  | float | 3 | 2 | 1
14908 | I3 |  |  | float | 3 | 2 | 1
14910 | In |  |  | float | 3 | 2 | 1
14912 | I THD1 |  |  | float | 3 | 2 | 1
14914 | I THD2 |  |  | float | 3 | 2 | 1
14916 | I THD3 |  |  | float | 3 | 2 | 1
14918 | I TDD1 |  |  | float | 3 | 2 | 1
14920 | I TDD2 |  |  | float | 3 | 2 | 1
14922 | I TDD3 |  |  | float | 3 | 2 | 1
14924 | K-factor 1 |  |  | float | 3 | 2 | 1
14926 | K-factor 2 |  |  | float | 3 | 2 | 1
14928 | K-factor 3 |  |  | float | 3 | 2 | 1
14930 | I Unbal Iu |  |  | float | 3 | 2 | 1
14932 | I Unbal Io |  |  | float | 3 | 2 | 1
14934 | kw imp |  |  | float | 3 | 2 | 1
14936 | kw exp |  |  | float | 3 | 2 | 1
14938 | kvar lag |  |  | float | 3 | 2 | 1
14940 | kvar lead |  |  | float | 3 | 2 | 1
14942 | kVA |  |  | float | 3 | 2 | 1
14944 | PF |  |  | float | 3 | 2 | 1
14946 | dPF |  |  | float | 3 | 2 | 1
14948 | temperature #1 |  |  | float | 3 | 2 | 1
14950 | temperature #2 |  |  | float | 3 | 2 | 1
14952 | temperature #3 |  |  | float | 3 | 2 | 1
14954 | temperature #4 |  |  | float | 3 | 2 | 1
14956 | temperature #5 |  |  | float | 3 | 2 | 1 | *통신이 끊어진 경우 복구를 위해 사용된다
14958 | Harmonics V1 |  |  | S16 | 3 | 1 | 24
14982 | Harmonics V2 |  |  | S16 | 3 | 1 | 24 | demand
15006 | Harmonics V3 |  |  | S16 | 3 | 1 | 24
15030 | Harmonics V12 |  |  | S16 | 3 | 1 | 24
15054 | Harmonics V23 |  |  | S16 | 3 | 1 | 24
15078 | Harmonics V31 |  |  | S16 | 3 | 1 | 24
15102 | Harmonics I1 |  |  | S16 | 3 | 1 | 24
15126 | Harmonics I2 |  |  | S16 | 3 | 1 | 24
15150 | Harmonics I3 |  |  | S16 | 3 | 1 | 24
15174 |  |  |  | U16 | 3 | 1 | 6
Energy log
15180 | Time Stamp |  |  | UTC | 3 | 2 | 1
15182 | kwh import |  |  | float | 3 | 2 | 1
15184 | kvarh lag |  |  | float | 3 | 2 | 1
15186 | kvarh lead |  |  | float | 3 | 2 | 1
15188 | kVAh |  |  | float | 3 | 2 | 1
15190 | energy log last day 01h |  |  | float | 3 | 2 | 4
15198 | energy log last day 02h |  |  | float | 3 | 2 | 4
15206 | energy log last day 03h |  |  | float | 3 | 2 | 4
15214 | energy log last day 04h |  |  | float | 3 | 2 | 4
15222 | energy log last day 05h |  |  | float | 3 | 2 | 4
15230 | energy log last day 06h |  |  | float | 3 | 2 | 4
15238 | energy log last day 07h |  |  | float | 3 | 2 | 4
15246 | energy log last day 08h |  |  | float | 3 | 2 | 4
15254 | energy log last day 09h |  |  | float | 3 | 2 | 4
15262 | energy log last day 10h |  |  | float | 3 | 2 | 4
15270 | energy log last day 11h |  |  | float | 3 | 2 | 4
15278 | energy log last day 12h |  |  | float | 3 | 2 | 4
15286 | energy log last day 13h |  |  | float | 3 | 2 | 4
15294 | energy log last day 14h |  |  | float | 3 | 2 | 4
15302 | energy log last day 15h |  |  | float | 3 | 2 | 4
15310 | energy log last day 16h |  |  | float | 3 | 2 | 4
15318 | energy log last day 17h |  |  | float | 3 | 2 | 4
15326 | energy log last day 18h |  |  | float | 3 | 2 | 4
15334 | energy log last day 19h |  |  | float | 3 | 2 | 4
15342 | energy log last day 20h |  |  | float | 3 | 2 | 4
15350 | energy log last day 21h |  |  | float | 3 | 2 | 4
15358 | energy log last day 22h |  |  | float | 3 | 2 | 4
15366 | energy log last day 23h |  |  | float | 3 | 2 | 4
15374 |  |  |  | U16 | 3 | 1 | 6
15380 | Time Stamp |  |  | UTC | 3 | 2 | 1
15382 | kwh import |  |  | float | 3 | 2 | 1
15384 | kvarh lag |  |  | float | 3 | 2 | 1
15386 | kvarh lead |  |  | float | 3 | 2 | 1
15388 | kVAh |  |  | float | 3 | 2 | 1
15390 | energy log this day 01h |  |  | float | 3 | 2 | 4
15398 | energy log this day 02h |  |  | float | 3 | 2 | 4
15406 | energy log this day 03h |  |  | float | 3 | 2 | 4
15414 | energy log this day 04h |  |  | float | 3 | 2 | 4
15422 | energy log this day 05h |  |  | float | 3 | 2 | 4
15430 | energy log this day 06h |  |  | float | 3 | 2 | 4
15438 | energy log this day 07h |  |  | float | 3 | 2 | 4
15446 | energy log this day 08h |  |  | float | 3 | 2 | 4
15454 | energy log this day 09h |  |  | float | 3 | 2 | 4
15462 | energy log this day 10h |  |  | float | 3 | 2 | 4
15470 | energy log this day 11h |  |  | float | 3 | 2 | 4
15478 | energy log this day 12h |  |  | float | 3 | 2 | 4
15486 | energy log this day 13h |  |  | float | 3 | 2 | 4
15494 | energy log this day 14h |  |  | float | 3 | 2 | 4 | 전일 디멘트 로그
15502 | energy log this day 15h |  |  | float | 3 | 2 | 4
15510 | energy log this day 16h |  |  | float | 3 | 2 | 4
15518 | energy log this day 17h |  |  | float | 3 | 2 | 4
15526 | energy log this day 18h |  |  | float | 3 | 2 | 4
15534 | energy log this day 19h |  |  | float | 3 | 2 | 4
15542 | energy log this day 20h |  |  | float | 3 | 2 | 4
15550 | energy log this day 21h |  |  | float | 3 | 2 | 4
15558 | energy log this day 22h |  |  | float | 3 | 2 | 4
15566 | energy log this day 23h |  |  | float | 3 | 2 | 4
15574 |  |  |  | U16 | 3 | 1 | 6
demand log last day
15580 | Time Stamp |  |  | U32 | 3 | 2 | 1
15582 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
15774 |  |  |  | U16 | 3 | 1 | 6
ITIC
15780 | fr |  |  | U16 | 3 | 1 | 1
15781 | re |  |  | U16 | 3 | 1 | 1
15782 | count |  |  | U16 | 3 | 1 | 1
15783 | SEQ |  |  | U16 | 3 | 1 | 1
15784 | Log #1 | start ts |  | UTC | 3 | 2 | 1
15786 |  | start ts(ms) |  | U16 | 3 | 1 | 1
15787 |  | duration |  | U16 | 3 | 1 | 1
15788 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
15789 |  | mask |  | U16 | 3 | 1 | 1
15790 |  | Level 1 |  | float | 3 | 2 | 1
15792 |  | Level 2 |  | float | 3 | 2 | 1
15794 |  | Level 3 |  | float | 3 | 2 | 1
15796 |  | Normal |  | float | 3 | 2 | 1
15798 | Log #2 |  |  | U16 | 3 | 1 | 14
15812 | Log #3 |  |  | U16 | 3 | 1 | 14
15826 | Log #4 |  |  | U16 | 3 | 1 | 14
15840 | Log #5 |  |  | U16 | 3 | 1 | 14
15854 | Log #6 |  |  | U16 | 3 | 1 | 14
15868 | Log #7 |  |  | U16 | 3 | 1 | 14
15882 | Log #8 |  |  | U16 | 3 | 1 | 14
15896 | Log #9 |  |  | U16 | 3 | 1 | 14
15910 | Log #10 |  |  | U16 | 3 | 1 | 14
15924 | Log #11 |  |  | U16 | 3 | 1 | 14
15938 | Log #12 |  |  | U16 | 3 | 1 | 14
15952 | Log #13 |  |  | U16 | 3 | 1 | 14
15966 | Log #14 |  |  | U16 | 3 | 1 | 14
15980 | Log #15 |  |  | U16 | 3 | 1 | 14
15994 | Log #16 |  |  | U16 | 3 | 1 | 14
16008 | Log #17 |  |  | U16 | 3 | 1 | 14
16022 | Log #18 |  |  | U16 | 3 | 1 | 14
16036 | Log #19 |  |  | U16 | 3 | 1 | 14
16050 | Log #20 |  |  | U16 | 3 | 1 | 14
16064 | Log #21 |  |  | U16 | 3 | 1 | 14
16078 | Log #22 |  |  | U16 | 3 | 1 | 14
16092 | Log #23 |  |  | U16 | 3 | 1 | 14
16106 | Log #24 |  |  | U16 | 3 | 1 | 14
16120 | Log #25 |  |  | U16 | 3 | 1 | 14
16134 | Log #26 |  |  | U16 | 3 | 1 | 14
16148 | Log #27 |  |  | U16 | 3 | 1 | 14
16162 | Log #28 |  |  | U16 | 3 | 1 | 14
16176 | Log #29 |  |  | U16 | 3 | 1 | 14
16190 | Log #30 |  |  | U16 | 3 | 1 | 14
16204 | Log #31 |  |  | U16 | 3 | 1 | 14
16218 | Log #32 |  |  | U16 | 3 | 1 | 14
16232 |  |  |  | U16 | 3 | 1 | 8
ITIC(Configurator)
16240 | fr |  |  | U16 | 3 | 1 | 1
16241 | re |  |  | U16 | 3 | 1 | 1
16242 | count |  |  | U16 | 3 | 1 | 1
16243 | reserved |  |  | U16 | 3 | 1 | 1
16244 | Log #1 | start ts |  | UTC | 3 | 2 | 1
16246 |  | start ts(ms) |  | U16 | 3 | 1 | 1
16247 |  | duration |  | U16 | 3 | 1 | 1
16248 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
16249 |  | mask |  | U16 | 3 | 1 | 1
16250 |  | Level 1 |  | float | 3 | 2 | 1
16252 |  | Level 2 |  | float | 3 | 2 | 1
16254 |  | Level 3 |  | float | 3 | 2 | 1
16256 |  | Normal |  | float | 3 | 2 | 1
16258 | Log #2 |  |  | U16 | 3 | 1 | 14
16272 | Log #3 |  |  | U16 | 3 | 1 | 14
16286 | Log #4 |  |  | U16 | 3 | 1 | 14
16300 | Log #5 |  |  | U16 | 3 | 1 | 14
16314 | Log #6 |  |  | U16 | 3 | 1 | 14
16328 | Log #7 |  |  | U16 | 3 | 1 | 14
16342 | Log #8 |  |  | U16 | 3 | 1 | 14
16356 | Log #9 |  |  | U16 | 3 | 1 | 14
16370 | Log #10 |  |  | U16 | 3 | 1 | 14
16384 | Log #11 |  |  | U16 | 3 | 1 | 14
16398 | Log #12 |  |  | U16 | 3 | 1 | 14
16412 | Log #13 |  |  | U16 | 3 | 1 | 14
16426 | Log #14 |  |  | U16 | 3 | 1 | 14
16440 | Log #15 |  |  | U16 | 3 | 1 | 14
16454 | Log #16 |  |  | U16 | 3 | 1 | 14
16468 | Log #17 |  |  | U16 | 3 | 1 | 14
16482 | Log #18 |  |  | U16 | 3 | 1 | 14
16496 | Log #19 |  |  | U16 | 3 | 1 | 14
16510 | Log #20 |  |  | U16 | 3 | 1 | 14
16524 | Log #21 |  |  | U16 | 3 | 1 | 14
16538 | Log #22 |  |  | U16 | 3 | 1 | 14
16552 | Log #23 |  |  | U16 | 3 | 1 | 14
16566 | Log #24 |  |  | U16 | 3 | 1 | 14
16580 | Log #25 |  |  | U16 | 3 | 1 | 14
16594 | Log #26 |  |  | U16 | 3 | 1 | 14
16608 | Log #27 |  |  | U16 | 3 | 1 | 14
16622 | Log #28 |  |  | U16 | 3 | 1 | 14
16636 | Log #29 |  |  | U16 | 3 | 1 | 14
16650 | Log #30 |  |  | U16 | 3 | 1 | 14
16664 | Log #31 |  |  | U16 | 3 | 1 | 14
16678 | Log #32 |  |  | U16 | 3 | 1 | 14
16692 |  |  |  | U16 | 3 | 1 | 8
Setting 영역 시작
PQ Event
16700 | OC Level | 정격의 2배 |  | U16 | 3,16 | 1 | 1
16701 | OC Cycle | unused |  | U16 | 3,16 | 1 | 1
16702 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
16703 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
16704 |  |  |  | U16 | 3,16 | 1 | 2
16706 | Sag Level(%), 90% | < 90% |  | U16 | 3,16 | 1 | 1
16707 | Sag Cycle | unused |  | U16 | 3,16 | 1 | 1
16708 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
16709 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
16710 |  |  |  | U16 | 3,16 | 1 | 2
16712 | Swell Level(%), 110~200~ | > 110% |  | U16 | 3,16 | 1 | 1
16713 | Swell Cycle | unused |  | U16 | 3,16 | 1 | 1
16714 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
16715 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
16716 |  |  |  | U16 | 3,16 | 1 | 2
16718 | Interruption Level, 5% | < 5% |  | U16 | 3,16 | 1 | 1
16719 | Interruption Time, 60s | unused |  | U16 | 3,16 | 1 | 1
16720 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
16721 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
16722 |  |  |  | U16 | 3,16 | 1 | 2
Transient Trigger
16724 | Transient Voltage, HoldOff Time, 20ms | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
16725 | Transient Voltage, Absolute Peak Level, 200% | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
16726 | Transient Voltage, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
16727 | Transient Voltage, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
16728 | Transient Current, HoldOff Time | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
16729 | Transient Current, Absolute Peak Level | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
16730 | Transient Current, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
16731 | Transient Current, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
16732 |  |  |  | U16 | 3,16 | 1 | 12
Recorder
Waveform
16744 | Recorder resolution(32k, 8k) |  |  | U16 | 3,16 | 1 | 1
16745 | Recorded paramater (U or I) |  |  | U16 | 3,16 | 1 | 1
16746 | pre trigger time(0.1s) |  |  | U16 | 3,16 | 1 | 1
16747 | post trigger time(1s) |  |  | U16 | 3,16 | 1 | 1
Disturbance
16748 | Recorder resolution (Half Cycle) |  |  | U16 | 3,16 | 1 | 1
16749 | Recorded parametrs(U or I) |  |  | U16 | 3,16 | 1 | 1
16750 | pre trigger time(100 sample) |  |  | U16 | 3,16 | 1 | 1
16751 | post trigger time(900 sample) |  |  | U16 | 3,16 | 1 | 1
16752 |  |  |  | U16 | 3,16 | 1 | 12
Trend Recorder
16764 | Trend Group #1 Active |  |  | U16 | 3,16 | 1 | 1
16765 | Trend Group #1 Storage Interval |  |  | U16 | 3,16 | 1 | 1
16766 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
16767 | Trend Group #1, Channel #1 |  |  | U16 | 3,16 | 1 | 1
16768 | Trend Group #1, Channel #2 |  |  | U16 | 3,16 | 1 | 1
16769 | Trend Group #1, Channel #3 |  |  | U16 | 3,16 | 1 | 1
16770 | Trend Group #1, Channel #4 |  |  | U16 | 3,16 | 1 | 1
16771 | Trend Group #1, Channel #5 |  |  | U16 | 3,16 | 1 | 1
16772 | Trend Group #1, Channel #6 |  |  | U16 | 3,16 | 1 | 1
16773 | Trend Group #1, Channel #7 |  |  | U16 | 3,16 | 1 | 1
16774 | Trend Group #1, Channel #8 |  |  | U16 | 3,16 | 1 | 1
16775 | Trend Group #1, Channel #9 |  |  | U16 | 3,16 | 1 | 1
16776 | Trend Group #1, Channel #10 |  |  | U16 | 3,16 | 1 | 1
16777 | Trend Group #1, Channel #11 |  |  | U16 | 3,16 | 1 | 1
16778 | Trend Group #1, Channel #12 |  |  | U16 | 3,16 | 1 | 1
16779 | Trend Group #1, Channel #13 |  |  | U16 | 3,16 | 1 | 1
16780 | Trend Group #1, Channel #14 |  |  | U16 | 3,16 | 1 | 1
16781 | Trend Group #1, Channel #15 |  |  | U16 | 3,16 | 1 | 1
16782 | Trend Group #1, Channel #16 |  |  | U16 | 3,16 | 1 | 1
16783 | Trend Group #2 Active |  |  | U16 | 3,16 | 1 | 1
16784 | Trend Group #2 Storage Interval |  |  | U16 | 3,16 | 1 | 1
16785 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
16786 | Trend Group #2, Channel #1 |  |  | U16 | 3,16 | 1 | 1
16787 | Trend Group #2, Channel #2 |  |  | U16 | 3,16 | 1 | 1
16788 | Trend Group #2, Channel #3 |  |  | U16 | 3,16 | 1 | 1
16789 | Trend Group #2, Channel #4 |  |  | U16 | 3,16 | 1 | 1
16790 | Trend Group #2, Channel #5 |  |  | U16 | 3,16 | 1 | 1
16791 | Trend Group #2, Channel #6 |  |  | U16 | 3,16 | 1 | 1
16792 | Trend Group #2, Channel #7 |  |  | U16 | 3,16 | 1 | 1
16793 | Trend Group #2, Channel #8 |  |  | U16 | 3,16 | 1 | 1
16794 | Trend Group #2, Channel #9 |  |  | U16 | 3,16 | 1 | 1
16795 | Trend Group #2, Channel #10 |  |  | U16 | 3,16 | 1 | 1
16796 | Trend Group #2, Channel #11 |  |  | U16 | 3,16 | 1 | 1
16797 | Trend Group #2, Channel #12 |  |  | U16 | 3,16 | 1 | 1
16798 | Trend Group #2, Channel #13 |  |  | U16 | 3,16 | 1 | 1
16799 | Trend Group #2, Channel #14 |  |  | U16 | 3,16 | 1 | 1
16800 | Trend Group #2, Channel #15 |  |  | U16 | 3,16 | 1 | 1
16801 | Trend Group #2, Channel #16 |  |  | U16 | 3,16 | 1 | 1
16802 | Trend Group #3 Active |  |  | U16 | 3,16 | 1 | 1
16803 | Trend Group #3 Storage Interval |  |  | U16 | 3,16 | 1 | 1
16804 |  |  |  | U16 | 3,16 | 1 | 1
16805 | Trend Group #3, Channel #1 |  |  | U16 | 3,16 | 1 | 1
16806 | Trend Group #3, Channel #2 |  |  | U16 | 3,16 | 1 | 1
16807 | Trend Group #3, Channel #3 |  |  | U16 | 3,16 | 1 | 1
16808 | Trend Group #3, Channel #4 |  |  | U16 | 3,16 | 1 | 1
16809 | Trend Group #3, Channel #5 |  |  | U16 | 3,16 | 1 | 1
16810 | Trend Group #3, Channel #6 |  |  | U16 | 3,16 | 1 | 1
16811 | Trend Group #3, Channel #7 |  |  | U16 | 3,16 | 1 | 1
16812 | Trend Group #3, Channel #8 |  |  | U16 | 3,16 | 1 | 1
16813 | Trend Group #3, Channel #9 |  |  | U16 | 3,16 | 1 | 1
16814 | Trend Group #3, Channel #10 |  |  | U16 | 3,16 | 1 | 1
16815 | Trend Group #3, Channel #11 |  |  | U16 | 3,16 | 1 | 1
16816 | Trend Group #3, Channel #12 |  |  | U16 | 3,16 | 1 | 1
16817 | Trend Group #3, Channel #13 |  |  | U16 | 3,16 | 1 | 1
16818 | Trend Group #3, Channel #14 |  |  | U16 | 3,16 | 1 | 1
16819 | Trend Group #3, Channel #15 |  |  | U16 | 3,16 | 1 | 1
16820 | Trend Group #3, Channel #16 |  |  | U16 | 3,16 | 1 | 1
16821 | Trend Group #4 Active |  |  | U16 | 3,16 | 1 | 1
16822 | Trend Group #4 Storage Interval |  |  | U16 | 3,16 | 1 | 1
16823 |  |  |  | U16 | 3,16 | 1 | 1
16824 | Trend Group #4, Channel #1 |  |  | U16 | 3,16 | 1 | 1
16825 | Trend Group #4, Channel #2 |  |  | U16 | 3,16 | 1 | 1
16826 | Trend Group #4, Channel #3 |  |  | U16 | 3,16 | 1 | 1
16827 | Trend Group #4, Channel #4 |  |  | U16 | 3,16 | 1 | 1
16828 | Trend Group #4, Channel #5 |  |  | U16 | 3,16 | 1 | 1
16829 | Trend Group #4, Channel #6 |  |  | U16 | 3,16 | 1 | 1
16830 | Trend Group #4, Channel #7 |  |  | U16 | 3,16 | 1 | 1
16831 | Trend Group #4, Channel #8 |  |  | U16 | 3,16 | 1 | 1
16832 | Trend Group #4, Channel #9 |  |  | U16 | 3,16 | 1 | 1
16833 | Trend Group #4, Channel #10 |  |  | U16 | 3,16 | 1 | 1
16834 | Trend Group #4, Channel #11 |  |  | U16 | 3,16 | 1 | 1
16835 | Trend Group #4, Channel #12 |  |  | U16 | 3,16 | 1 | 1
16836 | Trend Group #4, Channel #13 |  |  | U16 | 3,16 | 1 | 1
16837 | Trend Group #4, Channel #14 |  |  | U16 | 3,16 | 1 | 1
16838 | Trend Group #4, Channel #15 |  |  | U16 | 3,16 | 1 | 1
16839 | Trend Group #4, Channel #16 |  |  | U16 | 3,16 | 1 | 1
16840 |  |  |  | U16 | 3,16 | 1 | 4
Power Quality Report
16844 | Active |  |  | U16 | 3,16 | 1 | 1
16845 | Start Day |  |  | U16 | 3,16 | 1 | 1
16846 |  |  |  | U16 |  | 1 | 8
Alarm Definition
16854 | compare Time Delay(1s) |  |  | U16 | 3,16 | 1 | 1
16855 |  |  |  | U16 |  | 1 | 1
16856 |  |  |  | U16 |  | 1 | 1
16857 |  |  |  | U16 |  | 1 | 1
Alarm Settings
16858 | Alarm Info #1 Channel(0:disabled, >0: enabled) |  |  | U16 | 3,16 | 1 | 1
16859 | Alarm Cond (0: < , 1:>) |  |  | U16 | 3,16 | 1 | 1
16860 | Hysteresis (% of Nominal) |  |  | U16 | 3,16 | 1 | 1
16861 | Alarm Action (None, Relay or Beep) |  |  | U16 | 3,16 | 1 | 1
16862 | Alarm Level |  |  | float | 3,16 | 2 | 1
16864 | Alarm Settings #2 |  |  | U16 | 3,16 | 1 | 6
16870 | Alarm Settings #3 |  |  | U16 | 3,16 | 1 | 6
16876 | Alarm Settings #4 |  |  | U16 | 3,16 | 1 | 6
16882 | Alarm Settings #5 |  |  | U16 | 3,16 | 1 | 6
16888 | Alarm Settings #6 |  |  | U16 | 3,16 | 1 | 6
16894 | Alarm Settings #7 |  |  | U16 | 3,16 | 1 | 6
16900 | Alarm Settings #8 |  |  | U16 | 3,16 | 1 | 6
16906 | Alarm Settings #9 |  |  | U16 | 3,16 | 1 | 6
16912 | Alarm Settings #10 |  |  | U16 | 3,16 | 1 | 6
16918 | Alarm Settings #11 |  |  | U16 | 3,16 | 1 | 6
16924 | Alarm Settings #12 |  |  | U16 | 3,16 | 1 | 6
16930 | Alarm Settings #13 |  |  | U16 | 3,16 | 1 | 6
16936 | Alarm Settings #14 |  |  | U16 | 3,16 | 1 | 6
16942 | Alarm Settings #15 |  |  | U16 | 3,16 | 1 | 6
16948 | Alarm Settings #16 |  |  | U16 | 3,16 | 1 | 6
16954 | Alarm Settings #17 |  |  | U16 | 3,16 | 1 | 6
16960 | Alarm Settings #18 |  |  | U16 | 3,16 | 1 | 6
16966 | Alarm Settings #19 |  |  | U16 | 3,16 | 1 | 6
16972 | Alarm Settings #20 |  |  | U16 | 3,16 | 1 | 6
16978 | Alarm Settings #21 |  |  | U16 | 3,16 | 1 | 6
16984 | Alarm Settings #22 |  |  | U16 | 3,16 | 1 | 6
16990 | Alarm Settings #23 |  |  | U16 | 3,16 | 1 | 6
16996 | Alarm Settings #24 |  |  | U16 | 3,16 | 1 | 6
17002 | Alarm Settings #25 |  |  | U16 | 3,16 | 1 | 6
17008 | Alarm Settings #26 |  |  | U16 | 3,16 | 1 | 6
17014 | Alarm Settings #27 |  |  | U16 | 3,16 | 1 | 6
17020 | Alarm Settings #28 |  |  | U16 | 3,16 | 1 | 6
17026 | Alarm Settings #29 |  |  | U16 | 3,16 | 1 | 6
17032 | Alarm Settings #30 |  |  | U16 | 3,16 | 1 | 6
17038 | Alarm Settings #31 |  |  | U16 | 3,16 | 1 | 6
17044 | Alarm Settings #32 |  |  | U16 | 3,16 | 1 | 6
17050

## #3CH modbus
address | name | 설명 | Unit | TYPE | FC | Word Count | Item Count
Metering
20000 | Time Stamp |  |  | UTC | 3 | 2 | 1
20002 | TYPE |  |  | U16 | 3 | 1 | 1
20003 | STATUS | 1 : online, 0 : offline |  | U16 | 3 | 1 | 1
20004 | Frequency | 라인주파수 | Hz | float | 3 | 2 | 1
20006 | Internal Temp |  | ℃ | float | 3 | 2 | 1
20008 | U1 | 상전압 1 | V | float | 3 | 2 | 1
20010 | U2 | 상전압 2 |  | float | 3 | 2 | 1
20012 | U3 | 상전압 3 |  | float | 3 | 2 | 1
20014 | U~ | 상전압 평균 |  | float | 3 | 2 | 1
20016 | U12 | 선간 전압 12 |  | float | 3 | 2 | 1
20018 | U23 | 선간 전압 23 |  | float | 3 | 2 | 1
20020 | U31 | 선간 전압 31 |  | float | 3 | 2 | 1
20022 | Upp~ | 선간 전압 평균 |  | float | 3 | 2 | 1
20024 | Uunbalance2 |  | % | float | 3 | 2 | 1 | Uu=neg/pos*100
20026 | Uunbalance0 |  |  | float | 3 | 2 | 1 | Uo=zero/pos*100
20028 | U Zero Sequence Mag. |  |  | float | 3 | 2 | 1
20030 | U Zero Sequence angle |  |  | float | 3 | 2 | 1
20032 | U Positive Sequence Mag. |  |  | float | 3 | 2 | 1
20034 | U Positive Sequence angle |  |  | float | 3 | 2 | 1
20036 | U Negative Sequence Mag |  |  | float | 3 | 2 | 1
20038 | U Negative Sequence angle |  |  | float | 3 | 2 | 1
20040 | Angle U1 |  |  | float | 3 | 2 | 1
20042 | Angle U2 |  |  | float | 3 | 2 | 1
20044 | Angle U3 |  |  | float | 3 | 2 | 1
20046 | U Underdeviation L1 |  | % | float | 3 | 2 | 1
20048 | U Underdeviation L2 |  | % | float | 3 | 2 | 1
20050 | U Underdeviation L3 |  | % | float | 3 | 2 | 1
20052 | U Overdeviation L1 |  | % | float | 3 | 2 | 1
20054 | U Overdeviation L2 |  | % | float | 3 | 2 | 1
20056 | U Overdeviation L3 |  | % | float | 3 | 2 | 1
20058 | I1 | 상전류 1 | A | float | 3 | 2 | 1
20060 | I2 | 상전류 2 |  | float | 3 | 2 | 1
20062 | I3 | 상전류 3 |  | float | 3 | 2 | 1
20064 | I~ |  |  | float | 3 | 2 | 1
20066 | I total (I1+I2+I3) |  |  | float | 3 | 2 | 1
20068 | In(Measured) |  |  | float | 3 | 2 | 1 | 1. 5A: -3P4W(In) -3P3W(Ig), 2. AT/VT: Ig로 사용
20070 | In(Calculated) | Ia+Ib+Ic+In = Ig |  | float | 3 | 2 | 1 | 1. 5A: -3P4W(Ig=Ia+Ib+Ic+In), -3P3W(Ig=Ia+Ib+Ic), 2. AT/VT: 5A와 동일
20072 | Ig |  |  | float | 3 | 2 | 1
20074 | I Zero Sequence Mag |  |  | float | 3 | 2 | 1
20076 | I Zero Sequence angle |  |  | float | 3 | 2 | 1
20078 | I Positive Sequence Mag. |  |  | float | 3 | 2 | 1
20080 | I Positive Sequence angle |  |  | float | 3 | 2 | 1
20082 | I Negative Sequence Mag. |  |  | float | 3 | 2 | 1
20084 | I Negative Sequence angle |  |  | float | 3 | 2 | 1
20086 | Angle I1 |  |  | float | 3 | 2 | 1
20088 | Angle I2 |  |  | float | 3 | 2 | 1
20090 | Angle I3 |  |  | float | 3 | 2 | 1
20092 | Iunbalance2 |  | % | float | 3 | 2 | 1
20094 | Iunbalance0 |  |  | float | 3 | 2 | 1
20096 | P1 | 유효전력 P1 | W | float | 3 | 2 | 1
20098 | P2 | 유효전력 P2 |  | float | 3 | 2 | 1
20100 | P3 | 유효전력 P3 |  | float | 3 | 2 | 1
20102 | P total | 유효전력 P-total |  | float | 3 | 2 | 1
20104 | fP1 |  |  | float | 3 | 2 | 1
20106 | fP2 |  |  | float | 3 | 2 | 1
20108 | fP3 |  |  | float | 3 | 2 | 1
20110 | fP total |  |  | float | 3 | 2 | 1
20112 | Q1 | 무효전력 Q1 | VAR | float | 3 | 2 | 1
20114 | Q2 | 무효전력 Q2 |  | float | 3 | 2 | 1
20116 | Q3 | 무효전력 Q3 |  | float | 3 | 2 | 1
20118 | Q total | 무효전력 Q-total |  | float | 3 | 2 | 1
20120 | fQ1 |  |  | float | 3 | 2 | 1
20122 | fQ2 |  |  | float | 3 | 2 | 1
20124 | fQ3 |  |  | float | 3 | 2 | 1
20126 | fQ total |  |  | float | 3 | 2 | 1
20128 | S1 | 피상전력 S1 | VA | float | 3 | 2 | 1
20130 | S2 | 피상전력 S2 |  | float | 3 | 2 | 1
20132 | S3 | 피상전력 S3 |  | float | 3 | 2 | 1
20134 | S total | 피상전력 S-total |  | float | 3 | 2 | 1
20136 | fS1 |  |  | float | 3 | 2 | 1
20138 | fS2 |  |  | float | 3 | 2 | 1
20140 | fS3 |  |  | float | 3 | 2 | 1
20142 | fS total |  |  | float | 3 | 2 | 1
20144 | PF1 | 역률 PF1 | % | float | 3 | 2 | 1
20146 | PF2 | 역률 PF2 |  | float | 3 | 2 | 1
20148 | PF3 | 역률 PF3 |  | float | 3 | 2 | 1
20150 | PF total | 역률 PF-total |  | float | 3 | 2 | 1
20152 | dPF1 |  | % | float | 3 | 2 | 1
20154 | dPF2 |  |  | float | 3 | 2 | 1
20156 | dPF3 |  |  | float | 3 | 2 | 1
20158 | dPF total |  |  | float | 3 | 2 | 1
20160 | deformed Power D L1 |  | W | float | 3 | 2 | 1 | S=sqrt {P^{2}+Q^{2}+D^{2}}
20162 | deformed Power D L2 |  |  | float | 3 | 2 | 1
20164 | deformed Power D L3 |  |  | float | 3 | 2 | 1
20166 | deformed Power D Total |  |  | float | 3 | 2 | 1
20168 | Power Angle(atan(fPt,fQt) L1 |  | Degree | float | 3 | 2 | 1 | Angle between fundamental phase voltage and phase current
20170 | Power Angle(atan(fPt,fQt) L2 |  |  | float | 3 | 2 | 1
20172 | Power Angle(atan(fPt,fQt) L3 |  |  | float | 3 | 2 | 1
20174 |  |  |  | float | 3 | 2 | 1
20176 | THD V1 |  | % | float | 3 | 2 | 1
20178 | THD V2 |  |  | float | 3 | 2 | 1 | Chip에서 제공하는 결과 사용
20180 | THD V3 |  |  | float | 3 | 2 | 1
20182 | THD V12 |  |  | float | 3 | 2 | 1
20184 | THD V23 |  |  | float | 3 | 2 | 1
20186 | THD V31 |  |  | float | 3 | 2 | 1
20188 | CF V1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
20190 | CF V2 |  |  | float | 3 | 2 | 1
20192 | CF V3 |  |  | float | 3 | 2 | 1
20194 | CF V12 |  |  | float | 3 | 2 | 1
20196 | CF V23 |  |  | float | 3 | 2 | 1
20198 | CF V31 |  |  | float | 3 | 2 | 1
20200 | THD I1 |  |  | float | 3 | 2 | 1
20202 | THD I2 |  |  | float | 3 | 2 | 1
20204 | THD I3 |  |  | float | 3 | 2 | 1
20206 | TDD I1 |  |  | float | 3 | 2 | 1
20208 | TDD I2 |  |  | float | 3 | 2 | 1
20210 | TDD I3 |  |  | float | 3 | 2 | 1
20212 | K I1 | K-FACTOR : 고조파 허용율 |  | float | 3 | 2 | 1
20214 | K I2 |  |  | float | 3 | 2 | 1
20216 | K I3 |  |  | float | 3 | 2 | 1
20218 | CF I1 | Crest Factor : 파고율 |  | float | 3 | 2 | 1
20220 | CF I2 |  |  | float | 3 | 2 | 1
20222 | CF I3 |  |  | float | 3 | 2 | 1
20224 | fU1 | 기본파 U1 | V | float | 3 | 2 | 1
20226 | fU2 | 기본파 U2 |  | float | 3 | 2 | 1
20228 | fU3 | 기본파 U3 |  | float | 3 | 2 | 1
20230 | fU~ | 기본파 전압 평균 |  | float | 3 | 2 | 1
20232 | fI1 | 기본파 I1 | A | float | 3 | 2 | 1
20234 | fI2 | 기본파 I2 |  | float | 3 | 2 | 1
20236 | fI3 | 기본파 I3 |  | float | 3 | 2 | 1
20238 | fI~ | 기본파 전류 평균 |  | float | 3 | 2 | 1
Energy
20240 | import kwh(0 ~ 999,999,999.9 kw) TOTAL | 누적 TOTAL 유효전력량 |  | U32 | 3 | 2 | 1
20242 | export kwh TOTAL |  |  | U32 | 3 | 2 | 1
20244 | import kvarh TOTAL |  |  | U32 | 3 | 2 | 1
20246 | export kvarh TOTAL |  |  | U32 | 3 | 2 | 1
20248 | kvah TOTAL |  |  | U32 | 3 | 2 | 1
20250 |  |  |  | U32 | 3 | 2 | 1
20252 | import kwh(0 ~ 999,999,999.9 kw) L1 | 누적 L1 유효전력량 |  | U32 | 3 | 2 | 1
20254 | export kwh L1 |  |  | U32 | 3 | 2 | 1
20256 | import kvarh L1 |  |  | U32 | 3 | 2 | 1
20258 | export kvarh L1 |  |  | U32 | 3 | 2 | 1
20260 | kvah L1 |  |  | U32 | 3 | 2 | 1
20262 |  |  |  | U32 | 3 | 2 | 1
20264 | import kwh(0 ~ 999,999,999.9 kw) L2 | 누적 L2 유효전력량 |  | U32 | 3 | 2 | 1
20266 | export kwh L2 |  |  | U32 | 3 | 2 | 1
20268 | import kvarh L2 |  |  | U32 | 3 | 2 | 1
20270 | export kvarh L2 |  |  | U32 | 3 | 2 | 1
20272 | kvah L2 |  |  | U32 | 3 | 2 | 1
20274 |  |  |  | U32 | 3 | 2 | 1
20276 | import kwh(0 ~ 999,999,999.9 kw) L3 | 누적 L3 유효전력량 |  | U32 | 3 | 2 | 1
20278 | export kwh L3 |  |  | U32 | 3 | 2 | 1
20280 | import kvarh L3 |  |  | U32 | 3 | 2 | 1
20282 | export kvarh L3 |  |  | U32 | 3 | 2 | 1
20284 | kvah L3 |  |  | U32 | 3 | 2 | 1
20286 |  |  |  | U32 | 3 | 2 | 1
20288 | import kwh this month TOTAL | TOTAL THIS MONTH |  | U32 | 3 | 2 | 1
20290 | export kwh this month TOTAL |  |  | U32 | 3 | 2 | 1
20292 | import kvarh this month TOTAL |  |  | U32 | 3 | 2 | 1
20294 | export kvarh this month TOTAL |  |  | U32 | 3 | 2 | 1
20296 | kvah this month TOTAL |  |  | U32 | 3 | 2 | 1
20298 |  |  |  | U32 | 3 | 2 | 1
20300 | import kwh this month L1 | L1 THIS MONTH |  | U32 | 3 | 2 | 1
20302 | export kwh this month L1 |  |  | U32 | 3 | 2 | 1
20304 | import kvarh this month L1 |  |  | U32 | 3 | 2 | 1
20306 | export kvarh this month L1 |  |  | U32 | 3 | 2 | 1
20308 | kvah this month L1 |  |  | U32 | 3 | 2 | 1
20310 |  |  |  | U32 | 3 | 2 | 1
20312 | import kwh this month L2 | L2 THIS MONTH |  | U32 | 3 | 2 | 1
20314 | export kwh this month L2 |  |  | U32 | 3 | 2 | 1
20316 | import kvarh this month L2 |  |  | U32 | 3 | 2 | 1
20318 | export kvarh this month L2 |  |  | U32 | 3 | 2 | 1
20320 | kvah this month L2 |  |  | U32 | 3 | 2 | 1
20322 |  |  |  | U32 | 3 | 2 | 1
20324 | import kwh this month L3 | L3 THIS MONTH |  | U32 | 3 | 2 | 1
20326 | export kwh this month L3 |  |  | U32 | 3 | 2 | 1
20328 | import kvarh this month L3 |  |  | U32 | 3 | 2 | 1
20330 | export kvarh this month L3 |  |  | U32 | 3 | 2 | 1
20332 | kvah this month L3 |  |  | U32 | 3 | 2 | 1
20334 |  |  |  | U32 | 3 | 2 | 1
20336 | import kwh last month TOTAL | TOTAL LAST MONTH |  | U32 | 3 | 2 | 1
20338 | export kwh last month |  |  | U32 | 3 | 2 | 1
20340 | import kvarh last month |  |  | U32 | 3 | 2 | 1
20342 | export kvarh last month |  |  | U32 | 3 | 2 | 1
20344 | kvah last month |  |  | U32 | 3 | 2 | 1
20346 |  |  |  | U32 | 3 | 2 | 1
20348 | import kwh last month L1 | L1 LAST MONTH |  | U32 | 3 | 2 | 1
20350 | export kwh last month |  |  | U32 | 3 | 2 | 1
20352 | import kvarh last month |  |  | U32 | 3 | 2 | 1
20354 | export kvarh last month |  |  | U32 | 3 | 2 | 1
20356 | kvah last month |  |  | U32 | 3 | 2 | 1
20358 |  |  |  | U32 | 3 | 2 | 1
20360 | import kwh last month L2 | L2 LAST MONTH |  | U32 | 3 | 2 | 1
20362 | export kwh last month |  |  | U32 | 3 | 2 | 1
20364 | import kvarh last month |  |  | U32 | 3 | 2 | 1
20366 | export kvarh last month |  |  | U32 | 3 | 2 | 1
20368 | kvah last month |  |  | U32 | 3 | 2 | 1
20370 |  |  |  | U32 | 3 | 2 | 1
20372 | import kwh last month L3 | L3 LAST MONTH |  | U32 | 3 | 2 | 1
20374 | export kwh last month |  |  | U32 | 3 | 2 | 1
20376 | import kvarh last month |  |  | U32 | 3 | 2 | 1
20378 | export kvarh last month |  |  | U32 | 3 | 2 | 1
20380 | kvah last month |  |  | U32 | 3 | 2 | 1
20382 |  |  |  | U32 | 3 | 2 | 1
20384 | import kwh | TOTAL,L1,L2,L3 |  | U64 | 3 | 4 | 4
20400 | export kwh |  |  | U64 | 3 | 4 | 4
20416 | import kvarh |  |  | U64 | 3 | 4 | 4
20432 | export kvarh |  |  | U64 | 3 | 4 | 4
20448 | kvah |  |  | U64 | 3 | 4 | 4
20464 |  |  |  | U64 | 3 | 4 | 4
Demand
20480 | Time Stamp |  |  | UTC | 3 | 2 | 1
20482 | Max Demand P(import) |  |  | float | 3 | 2 | 1
20484 | Time Stamp |  |  | UTC | 3 | 2 | 1
20486 | Max Demand P(export) |  |  | float | 3 | 2 | 1
20488 | Time Stamp |  |  | UTC | 3 | 2 | 1
20490 | Max Demand Q(import) |  |  | float | 3 | 2 | 1
20492 | Time Stamp |  |  | UTC | 3 | 2 | 1
20494 | Max Demand Q(export) |  |  | float | 3 | 2 | 1
20496 | Time Stamp |  |  | UTC | 3 | 2 | 1
20498 | Max Demand S |  |  | float | 3 | 2 | 1
20500 | Time Stamp |  |  | UTC | 3 | 2 | 1
20502 | Max Demand I1 |  |  | float | 3 | 2 | 1
20504 | Time Stamp |  |  | UTC | 3 | 2 | 1
20506 | Max Demand I2 |  |  | float | 3 | 2 | 1
20508 | Time Stamp |  |  | UTC | 3 | 2 | 1
20510 | Max Demand I3 |  |  | float | 3 | 2 | 1
20512 | Demand time stamp |  |  | UTC | 3 | 2 | 1
20514 | Demand P(import) |  |  | float | 3 | 2 | 1
20516 | Demand P(export) |  |  | float | 3 | 2 | 1 | 최근 24시간 그래프 그린다
20518 | Demand Q(import) |  |  | float | 3 | 2 | 1
20520 | Demand Q(export) |  |  | float | 3 | 2 | 1
20522 | Demand S(export) |  |  | float | 3 | 2 | 1
20524 | Demand I1 |  |  | float | 3 | 2 | 1
20526 | Demand I2 |  |  | float | 3 | 2 | 1
20528 | Demand I3 |  |  | float | 3 | 2 | 1
20530 | Present Demand P(import) |  |  | float | 3 | 2 | 1
20532 | Present Demand P(export) |  |  | float | 3 | 2 | 1
20534 | Present Demand Q(import) |  |  | float | 3 | 2 | 1
20536 | Present Demand Q(export) |  |  | float | 3 | 2 | 1
20538 | Present Demand S(export) |  |  | float | 3 | 2 | 1
20540 | Forecast Demand P(export) |  |  | float | 3 | 2 | 1
20542 | Demand P 15m(import) |  |  | float | 3 | 2 | 1
20544 |  |  |  | float | 3 | 2 | 1
20546 |  |  |  | float | 3 | 2 | 1
20548 | Time Stamp(Demand Log 시작일) |  |  | U32 | 3 | 2 | 1
20550 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
20742 |  |  |  | float | 3 | 2 | 19
Voltage Quality RealTime Value
20780 | Voltage Under Deviation L1 |  | % | float | 3 | 2 | 1
20782 | Voltage Under Deviation L2 |  | % | float | 3 | 2 | 1
20784 | Voltage Under Deviation L3 |  | % | float | 3 | 2 | 1
20786 | Voltage Under Value L1 |  | rms | float | 3 | 2 | 1
20788 | Voltage Under Value L2 |  | rms | float | 3 | 2 | 1
20790 | Voltage Under Value L3 |  | rms | float | 3 | 2 | 1
20792 | Voltage Over Deviation L1 |  | % | float | 3 | 2 | 1
20794 | Voltage Over Deviation L2 |  | % | float | 3 | 2 | 1
20796 | Voltage Over Deviation L3 |  | % | float | 3 | 2 | 1
20798 | Voltage Over Value L1 |  | rms | float | 3 | 2 | 1
20800 | Voltage Over Value L2 |  | rms | float | 3 | 2 | 1
20802 | Voltage Over Value L3 |  | rms | float | 3 | 2 | 1
20804 | Flickers Pi L1 | 150/180 Cycles |  | float | 3 | 2 | 1
20806 | Flickers Pi L2 |  |  | float | 3 | 2 | 1
20808 | Flickers Pi L3 |  |  | float | 3 | 2 | 1
20810 | Flicker Pst L1 | 10min |  | float | 3 | 2 | 1
20812 | Flicker Pst L2 |  |  | float | 3 | 2 | 1
20814 | Flicker Pst L3 |  |  | float | 3 | 2 | 1
20816 | Flicker Plt L1 | 2hr |  | float | 3 | 2 | 1 | 최근 24시간 그래프 그린다
20818 | Flicker Plt L2 |  |  | float | 3 | 2 | 1
20820 | Flicker Plt L3 |  |  | float | 3 | 2 | 1
20822 | Signaling Volt L1 | Magnitude of current 10/12 cycles as a percentage of nominal voltage. |  | float | 3 | 2 | 1
20824 | Signaling Volt L2 |  |  | float | 3 | 2 | 1
20826 | Signaling Volt L3 |  |  | float | 3 | 2 | 1
20828 | Signaling Volt Max L1 | Maximum magnitude of MSV from recording started as a percentage of nominal voltage |  | float | 3 | 2 | 1
20830 | Signaling Volt Max L2 |  |  | float | 3 | 2 | 1
20832 | Signaling Volt Max L3 |  |  | float | 3 | 2 | 1
20834 |  |  |  | float | 3 | 2 | 23
EN50160 This Week
20880 | start date |  |  | UTC | 3 | 2 | 1
20882 | end date |  |  | UTC | 3 | 2 | 1
20884 | status&compliance | bit 0: Freq Var1 bit 1: Freq Var2 bit 2: Volt Var1 L1 bit 3: Volt Var1 L2 bit 4: Volt Var1 L3 bit 5: Volt Var2 L1 bit 6: Volt Var2 L2 bit 7: Volt Var2 L3 bit 8: Unbalance bit 9: Volt THD L1 bit 10: Volt THD L2 bit 11: Volt THD L3 bit 12: Volt HD L1 bit 13: Volt HD L2 bit 14: Volt HD L3 bit 15: Pst L1 bit 16: Pst L2 bit 17: Pst L3 bit 18: Plt L1 bit 19: Plt L2 bit 20: Plt L3 bit 21: SigVolt L1 bit 22: SigVolt L2 bit 23: SigVolt L3 bit 31: Complete [status] 0: OK 1: failed |  | U32 | 3 | 2 | 1
20886 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1 | 95%/Week
20887 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1 | Info Only
20888 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
20889 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
20890 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
20891 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
20892 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
20893 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1 | Info Only
20894 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
20895 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
20896 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
20897 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
20898 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
20899 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
20900 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
20901 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
20902 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1 | Info Only
20903 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
20904 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
20905 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
20906 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
20907 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
20908 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1 | 95%/Week
20909 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
20910 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
20911 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1 | 99%/Day
20912 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
20913 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
20914 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
20915 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
20916 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
20917 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
20918 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
20919 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
20920 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
20921 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
20922 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
20923 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
20924 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
20925 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
20926 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
20927 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
20928 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
20929 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
EN50160 Last Week
20930 | start date |  |  | UTC | 3 | 2 | 1
20932 | end date |  |  | UTC | 3 | 2 | 1
20934 | status |  |  | U16 | 3 | 1 | 1
20935 | compilance |  |  | U16 | 3 | 1 | 1
20936 | Frequency Variation 1(%) | 0 |  | U16 | 3 | 1 | 1
20937 | Frequency Variation 2(%) | 1 |  | U16 | 3 | 1 | 1
20938 | Voltage Variation 1 L1(%) | 2 |  | U16 | 3 | 1 | 1
20939 | Voltage Variation 1 L2(%) |  |  | U16 | 3 | 1 | 1
20940 | Voltage Variation 1 L3(%) |  |  | U16 | 3 | 1 | 1
20941 | Voltage Variation 2 L1(%) | 3 |  | U16 | 3 | 1 | 1
20942 | Voltage Variation 2 L2(%) |  |  | U16 | 3 | 1 | 1
20943 | Voltage Variation 2 L3(%) |  |  | U16 | 3 | 1 | 1
20944 | Voltage Unbalance(%) | 4 |  | U16 | 3 | 1 | 1
20945 | THDs Variation L1(%) | 5 |  | U16 | 3 | 1 | 1
20946 | THDs Variation L2(%) |  |  | U16 | 3 | 1 | 1
20947 | THDs Variation L3(%) |  |  | U16 | 3 | 1 | 1
20948 | Harmonics Variatiopn L1(%) | 6 |  | U16 | 3 | 1 | 1
20949 | Harmonics Variatiopn L2(%) |  |  | U16 | 3 | 1 | 1
20950 | Harmonics Variatiopn L3(%) |  |  | U16 | 3 | 1 | 1
20951 | Flickers Pst L1(%) | 7 |  | U16 | 3 | 1 | 1
20952 | Flickers Pst L2(%) |  |  | U16 | 3 | 1 | 1
20953 | Flickers Pst L3(%) |  |  | U16 | 3 | 1 | 1
20954 | Flickers Plt L1(%) | 8 |  | U16 | 3 | 1 | 1
20955 | Flickers Plt L2(%) |  |  | U16 | 3 | 1 | 1
20956 | Flickers Plt L3(%) |  |  | U16 | 3 | 1 | 1
20957 | Signaling Voltage L1(%) | 9 |  | U16 | 3 | 1 | 1
20958 | Signaling Voltage L2(%) |  |  | U16 | 3 | 1 | 1
20959 | Signaling Voltage L3(%) |  |  | U16 | 3 | 1 | 1
20960 | Voltage Dips L1 |  |  | U16 | 3 | 1 | 1
20961 | Voltage Dips L2 |  |  | U16 | 3 | 1 | 1
20962 | Voltage Dips L3 |  |  | U16 | 3 | 1 | 1
20963 | Voltage Dips Multi Phase |  |  | U16 | 3 | 1 | 1
20964 | Voltage Swells L1 |  |  | U16 | 3 | 1 | 1
20965 | Voltage Swells L2 |  |  | U16 | 3 | 1 | 1
20966 | Voltage Swells L3 |  |  | U16 | 3 | 1 | 1
20967 | Voltage Swells Multi Phase |  |  | U16 | 3 | 1 | 1
20968 | Short Interruptions L1 |  |  | U16 | 3 | 1 | 1
20969 | Short Interruptions L2 |  |  | U16 | 3 | 1 | 1
20970 | Short Interruptions L3 |  |  | U16 | 3 | 1 | 1
20971 | Short Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
20972 | Long Interruptions L1 |  |  | U16 | 3 | 1 | 1
20973 | Long Interruptions L2 |  |  | U16 | 3 | 1 | 1
20974 | Long Interruptions L3 |  |  | U16 | 3 | 1 | 1
20975 | Long Interruptions Multi Phase |  |  | U16 | 3 | 1 | 1
20976 | Rapid Voltage Changes L1 |  |  | U16 | 3 | 1 | 1
20977 | Rapid Voltage Changes L2 |  |  | U16 | 3 | 1 | 1
20978 | Rapid Voltage Changes L3 |  |  | U16 | 3 | 1 | 1
20979 | Rapid Voltage Changes Multi Phase |  |  | U16 | 3 | 1 | 1
Harmonics
20980 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
21044 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
21108 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
21172 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
21236 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
21300 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
21364 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
21428 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
21492 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
21556 |  |  |  | S16 | 3 | 1 | 24
Inter Harmonics
21580 | Harmonics V1 |  |  | S16 | 3 | 1 | 64
21644 | Harmonics V2 |  |  | S16 | 3 | 1 | 64
21708 | Harmonics V3 |  |  | S16 | 3 | 1 | 64
21772 | Harmonics V12 |  |  | S16 | 3 | 1 | 64
21836 | Harmonics V23 |  |  | S16 | 3 | 1 | 64
21900 | Harmonics V31 |  |  | S16 | 3 | 1 | 64
21964 | Harmonics I1 |  |  | S16 | 3 | 1 | 64
22028 | Harmonics I2 |  |  | S16 | 3 | 1 | 64
22092 | Harmonics I3 |  |  | S16 | 3 | 1 | 64
22156 |  |  |  | S16 | 3 | 1 | 24
Max/Min
22180 | fr |  |  | U16 | 3 | 1 | 1
22181 | re |  |  | U16 | 3 | 1 | 1
22182 | Reset TimeStamp |  |  | UTC | 3 | 2 | 1
22184 | Frequency | Max |  | float | 3 | 2 | 1
22186 |  | Max Timestamp |  | UTC | 3 | 2 | 1
22188 |  | Min |  | float | 3 | 2 | 1
22190 |  | Min Timestamp |  | UTC | 3 | 2 | 1
22192 | Temp |  |  | float | 3 | 2 | 4
22200 | U1 |  |  | float | 3 | 2 | 4
22208 | U2 |  |  | float | 3 | 2 | 4
22216 | U3 |  |  | float | 3 | 2 | 4 | http://www.relaytech.com/symcomp_calculator.htm
22224 | U~ |  |  | float | 3 | 2 | 4
22232 | U12 |  |  | float | 3 | 2 | 4
22240 | U23 |  |  | float | 3 | 2 | 4
22248 | U31 |  |  | float | 3 | 2 | 4
22256 | Upp~ |  |  | float | 3 | 2 | 4
22264 | I1 |  |  | float | 3 | 2 | 4
22272 | I2 |  |  | float | 3 | 2 | 4
22280 | I3 |  |  | float | 3 | 2 | 4
22288 | I~ |  |  | float | 3 | 2 | 4
22296 | I total |  |  | float | 3 | 2 | 4
22304 | In |  |  | float | 3 | 2 | 4
22312 | Isum |  |  | float | 3 | 2 | 4
22320 | P1 |  |  | float | 3 | 2 | 4
22328 | P2 |  |  | float | 3 | 2 | 4
22336 | P3 |  |  | float | 3 | 2 | 4
22344 | P total |  |  | float | 3 | 2 | 4
22352 | Q1 |  |  | float | 3 | 2 | 4
22360 | Q2 |  |  | float | 3 | 2 | 4
22368 | Q3 |  |  | float | 3 | 2 | 4
22376 | Q total |  |  | float | 3 | 2 | 4
22384 | S1 |  |  | float | 3 | 2 | 4
22392 | S2 |  |  | float | 3 | 2 | 4
22400 | S3 |  |  | float | 3 | 2 | 4
22408 | S total |  |  | float | 3 | 2 | 4
22416 | PF L1 |  |  | float | 3 | 2 | 4
22424 | PF L2 |  |  | float | 3 | 2 | 4
22432 | PF L3 |  |  | float | 3 | 2 | 4
22440 | PF total |  |  | float | 3 | 2 | 4
22448 | THD U1 |  |  | float | 3 | 2 | 4
22456 | THD U2 |  |  | float | 3 | 2 | 4
22464 | THD U3 |  |  | float | 3 | 2 | 4
22472 | THD U12 |  |  | float | 3 | 2 | 4
22480 | THD U23 |  |  | float | 3 | 2 | 4
22488 | THD U31 |  |  | float | 3 | 2 | 4
22496 | THD I1 |  |  | float | 3 | 2 | 4
22504 | THD I2 |  |  | float | 3 | 2 | 4
22512 | THD I3 |  |  | float | 3 | 2 | 4
22520 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
22522 | reserved |  |  | U16 | 3 | 1 | 1
22523 | CRC |  |  | U16 | 3 | 1 | 1
22524 |  |  |  | U16 | 3 | 1 | 6
alarm status
22530 | fr |  |  | U16 | 3 | 1 | 1
22531 | re |  |  | U16 | 3 | 1 | 1
22532 | reset Ts |  |  | UTC | 3 | 2 | 1
22534 | Alarm State #1 | Alarm Channel |  | U16 | 3 | 1 | 1
22535 |  | Alarm Condition |  | U16 | 3 | 1 | 1
22536 |  | Alarm Level |  | float | 3 | 2 | 1
22538 |  | Alarm Status |  | U16 | 3 | 1 | 1
22539 |  | Alarm Count |  | U16 | 3 | 1 | 1
22540 | Alarm State #2 |  |  | U16 | 3 | 1 | 6
22546 | Alarm State #3 |  |  | U16 | 3 | 1 | 6
22552 | Alarm State #4 |  |  | U16 | 3 | 1 | 6
22558 | Alarm State #5 |  |  | U16 | 3 | 1 | 6
22564 | Alarm State #6 |  |  | U16 | 3 | 1 | 6
22570 | Alarm State #7 |  |  | U16 | 3 | 1 | 6
22576 | Alarm State #8 |  |  | U16 | 3 | 1 | 6
22582 | Alarm State #9 |  |  | U16 | 3 | 1 | 6
22588 | Alarm State #10 |  |  | U16 | 3 | 1 | 6
22594 | Alarm State #11 |  |  | U16 | 3 | 1 | 6
22600 | Alarm State #12 |  |  | U16 | 3 | 1 | 6
22606 | Alarm State #13 |  |  | U16 | 3 | 1 | 6
22612 | Alarm State #14 |  |  | U16 | 3 | 1 | 6
22618 | Alarm State #15 |  |  | U16 | 3 | 1 | 6
22624 | Alarm State #16 |  |  | U16 | 3 | 1 | 6
22630 | Alarm State #17 |  |  | U16 | 3 | 1 | 6
22636 | Alarm State #18 |  |  | U16 | 3 | 1 | 6
22642 | Alarm State #19 |  |  | U16 | 3 | 1 | 6
22648 | Alarm State #20 |  |  | U16 | 3 | 1 | 6
22654 | Alarm State #21 |  |  | U16 | 3 | 1 | 6
22660 | Alarm State #22 |  |  | U16 | 3 | 1 | 6
22666 | Alarm State #23 |  |  | U16 | 3 | 1 | 6
22672 | Alarm State #24 |  |  | U16 | 3 | 1 | 6
22678 | Alarm State #25 |  |  | U16 | 3 | 1 | 6
22684 | Alarm State #26 |  |  | U16 | 3 | 1 | 6
22690 | Alarm State #27 |  |  | U16 | 3 | 1 | 6
22696 | Alarm State #28 |  |  | U16 | 3 | 1 | 6
22702 | Alarm State #29 |  |  | U16 | 3 | 1 | 6
22708 | Alarm State #30 |  |  | U16 | 3 | 1 | 6
22714 | Alarm State #31 |  |  | U16 | 3 | 1 | 6
22720 | Alarm State #32 |  |  | U16 | 3 | 1 | 6
22726 | update Ts |  |  | U32 | 3 | 2 | 1
22728 | Global Alarm Status | (alarm 하나라도 있으면 1, 아니면 0) |  | U16 | 3 | 1 | 1
22729 |  |  |  | U16 | 3 | 1 | 1
alarm log
22730 | fr | 0 ~ 1023 |  | U16 | 3 | 1 | 1
22731 | re | 0 ~ 1023 |  | U16 | 3 | 1 | 1
22732 | count | 전체 log 수 |  | U16 | 3 | 1 | 1
22733 | seq |  |  | U16 | 3 | 1 | 1
22734 | Alarm Log #1 | Time Stamp |  | UTC | 3 | 2 | 1 | 2019-5-11변경
22736 |  | status |  | U16 | 3 | 1 | 1
22737 |  | Alarm Channel & Condition |  | U16 | 3 | 1 | 1
22738 |  | level |  | float | 3 | 2 | 1
22740 |  | Value |  | float | 3 | 2 | 1
22742 | Alarm Log #2 |  |  | U16 | 3 | 1 | 8
22750 | Alarm Log #3 |  |  | U16 | 3 | 1 | 8
22758 | Alarm Log #4 |  |  | U16 | 3 | 1 | 8
22766 | Alarm Log #5 |  |  | U16 | 3 | 1 | 8
22774 | Alarm Log #6 |  |  | U16 | 3 | 1 | 8
22782 | Alarm Log #7 |  |  | U16 | 3 | 1 | 8
22790 | Alarm Log #8 |  |  | U16 | 3 | 1 | 8
22798 | Alarm Log #9 |  |  | U16 | 3 | 1 | 8
22806 | Alarm Log #10 |  |  | U16 | 3 | 1 | 8
22814 | Alarm Log #11 |  |  | U16 | 3 | 1 | 8
22822 | Alarm Log #12 |  |  | U16 | 3 | 1 | 8
22830 | Alarm Log #13 |  |  | U16 | 3 | 1 | 8
22838 | Alarm Log #14 |  |  | U16 | 3 | 1 | 8
22846 | Alarm Log #15 |  |  | U16 | 3 | 1 | 8
22854 | Alarm Log #16 |  |  | U16 | 3 | 1 | 8
22862 | Alarm Log #17 |  |  | U16 | 3 | 1 | 8
22870 | Alarm Log #18 |  |  | U16 | 3 | 1 | 8
22878 | Alarm Log #19 |  |  | U16 | 3 | 1 | 8
22886 | Alarm Log #20 |  |  | U16 | 3 | 1 | 8
22894 | Alarm Log #21 |  |  | U16 | 3 | 1 | 8
22902 | Alarm Log #22 |  |  | U16 | 3 | 1 | 8
22910 | Alarm Log #23 |  |  | U16 | 3 | 1 | 8
22918 | Alarm Log #24 |  |  | U16 | 3 | 1 | 8
22926 | Alarm Log #25 |  |  | U16 | 3 | 1 | 8
22934 | Alarm Log #26 |  |  | U16 | 3 | 1 | 8
22942 | Alarm Log #27 |  |  | U16 | 3 | 1 | 8
22950 | Alarm Log #28 |  |  | U16 | 3 | 1 | 8
22958 | Alarm Log #29 |  |  | U16 | 3 | 1 | 8
22966 | Alarm Log #30 |  |  | U16 | 3 | 1 | 8
22974 | Alarm Log #31 |  |  | U16 | 3 | 1 | 8
22982 | Alarm Log #32 |  |  | U16 | 3 | 1 | 8
22990 |  |  |  | U16 | 3 | 1 | 40
이벤트 리스트
23030 | fr | 0 ~ 1023 |  | U16 | 3 | 1 | 1
23031 | re | 0 ~ 1023 |  | U16 | 3 | 1 | 1
23032 | count | 0 ~ 1023 |  | U16 | 3 | 1 | 1
23033 | seq |  |  | U16 | 3 | 1 | 1
PQ 이벤트(Sag, Swell, Transient, OC)
23034 | start ts |  |  | UTC | 3 | 2 | 1
23036 | start ts(ms) |  |  | U16 | 3 | 1 | 1
23037 | duration |  |  | U16 | 3 | 1 | 1
23038 | type | 1 : E_SAG 2 : E_SWELL 3 : E_sINTR 4 : E_lINTR 5 : E_OC 6 : E_RVC 7 : E_TrV 8 : E_TrC |  | U16 | 3 | 1 | 1
23039 | mask |  |  | U16 | 3 | 1 | 1
23040 | Level 1 |  |  | float | 3 | 2 | 1
23042 | Level 2 |  |  | float | 3 | 2 | 1
23044 | Level 3 |  |  | float | 3 | 2 | 1
23046 | PQ Event #2 |  |  | U16 | 3 | 1 | 12
23058 | PQ Event #3 |  |  | U16 | 3 | 1 | 12
23070 | PQ Event #4 |  |  | U16 | 3 | 1 | 12
23082 | PQ Event #5 |  |  | U16 | 3 | 1 | 12
23094 | PQ Event #6 |  |  | U16 | 3 | 1 | 12
23106 | PQ Event #7 |  |  | U16 | 3 | 1 | 12
23118 | PQ Event #8 |  |  | U16 | 3 | 1 | 12
23130 | PQ Event #9 |  |  | U16 | 3 | 1 | 12
23142 | PQ Event #10 |  |  | U16 | 3 | 1 | 12
23154 | PQ Event #11 |  |  | U16 | 3 | 1 | 12
23166 | PQ Event #12 |  |  | U16 | 3 | 1 | 12
23178 | PQ Event #13 |  |  | U16 | 3 | 1 | 12
23190 | PQ Event #14 |  |  | U16 | 3 | 1 | 12
23202 | PQ Event #15 |  |  | U16 | 3 | 1 | 12
23214 | PQ Event #16 |  |  | U16 | 3 | 1 | 12
23226 | PQ Event #17 |  |  | U16 | 3 | 1 | 12
23238 | PQ Event #18 |  |  | U16 | 3 | 1 | 12
23250 | PQ Event #19 |  |  | U16 | 3 | 1 | 12
23262 | PQ Event #20 |  |  | U16 | 3 | 1 | 12
23274 | PQ Event #21 |  |  | U16 | 3 | 1 | 12
23286 | PQ Event #22 |  |  | U16 | 3 | 1 | 12
23298 | PQ Event #23 |  |  | U16 | 3 | 1 | 12
23310 | PQ Event #24 |  |  | U16 | 3 | 1 | 12
23322 | PQ Event #25 |  |  | U16 | 3 | 1 | 12
23334 | PQ Event #26 |  |  | U16 | 3 | 1 | 12
23346 | PQ Event #27 |  |  | U16 | 3 | 1 | 12
23358 | PQ Event #28 |  |  | U16 | 3 | 1 | 12
23370 | PQ Event #29 |  |  | U16 | 3 | 1 | 12
23382 | PQ Event #30 |  |  | U16 | 3 | 1 | 12
23394 | PQ Event #31 |  |  | U16 | 3 | 1 | 12
23406 | PQ Event #32 |  |  | U16 | 3 | 1 | 12
23418 |  |  |  | U16 | 3 | 1 | 2
PQ Event Counter
23420 |  |  |  | U16 | 3 | 1 | 1
23421 |  |  |  | U16 | 3 | 1 | 1
23422 |  |  |  | U16 | 3 | 1 | 1
23423 | Sag Coount |  |  | U16 | 3 | 1 | 1
23424 | Swell Count |  |  | U16 | 3 | 1 | 1
23425 |  |  |  | U16 | 3 | 1 | 1
23426 |  |  |  | U16 | 3 | 1 | 1
23427 |  |  |  | U16 | 3 | 1 | 1
23428 |  |  |  | U16 | 3 | 1 | 1
23429 |  |  |  | U16 | 3 | 1 | 1
Wave Sample | [7 empty] | 32K: 67,107,786 8K: 74,518,668 첫번째 번지 접근시 wave data를 modbus map으로 load 한다
23430 | Wave Form V1 (160 sample) |  |  | S16 | 3 | 1 | 160
23590 | Wave Form V2 (160 sample) |  |  | S16 | 3 | 1 | 160
23750 | Wave Form V3 (160 sample) |  |  | S16 | 3 | 1 | 160
23910 | Wave Form V12 (160 sample) |  |  | S16 | 3 | 1 | 160
24070 | Wave Form V23 (160 sample) |  |  | S16 | 3 | 1 | 160
24230 | Wave Form V31 (160 sample) |  |  | S16 | 3 | 1 | 160
24390 | Wave Form I1 (160 sample) |  |  | S16 | 3 | 1 | 160
24550 | Wave Form I2 (160 sample) |  |  | S16 | 3 | 1 | 160
24710 | Wave Form I3 (160 sample) |  |  | S16 | 3 | 1 | 160
24870 | vscale |  |  | float | 3 | 2 | 1
24872 | iscale |  |  | float | 3 | 2 | 1
24874 |  |  |  | S16 | 3 | 1 | 6
월간리포트 생성위한 10분 평균
24880 | Update TimeStamp |  |  | UTC | 3 | 2 | 1
24882 | U1 |  |  | float | 3 | 2 | 1
24884 | U2 |  |  | float | 3 | 2 | 1
24886 | U3 |  |  | float | 3 | 2 | 1
24888 | U THD1 |  |  | float | 3 | 2 | 1
24890 | U THD2 |  |  | float | 3 | 2 | 1
24892 | U THD3 |  |  | float | 3 | 2 | 1
24894 | Upp THD1 |  |  | float | 3 | 2 | 1
24896 | Upp THD2 |  |  | float | 3 | 2 | 1
24898 | Upp THD3 |  |  | float | 3 | 2 | 1
24900 | U Unbal Uu |  |  | float | 3 | 2 | 1
24902 | U Unbal Uo |  |  | float | 3 | 2 | 1
24904 | I1 |  |  | float | 3 | 2 | 1
24906 | I2 |  |  | float | 3 | 2 | 1
24908 | I3 |  |  | float | 3 | 2 | 1
24910 | In |  |  | float | 3 | 2 | 1
24912 | I THD1 |  |  | float | 3 | 2 | 1
24914 | I THD2 |  |  | float | 3 | 2 | 1
24916 | I THD3 |  |  | float | 3 | 2 | 1
24918 | I TDD1 |  |  | float | 3 | 2 | 1
24920 | I TDD2 |  |  | float | 3 | 2 | 1
24922 | I TDD3 |  |  | float | 3 | 2 | 1
24924 | K-factor 1 |  |  | float | 3 | 2 | 1
24926 | K-factor 2 |  |  | float | 3 | 2 | 1
24928 | K-factor 3 |  |  | float | 3 | 2 | 1
24930 | I Unbal Iu |  |  | float | 3 | 2 | 1
24932 | I Unbal Io |  |  | float | 3 | 2 | 1
24934 | kw imp |  |  | float | 3 | 2 | 1
24936 | kw exp |  |  | float | 3 | 2 | 1
24938 | kvar lag |  |  | float | 3 | 2 | 1
24940 | kvar lead |  |  | float | 3 | 2 | 1
24942 | kVA |  |  | float | 3 | 2 | 1
24944 | PF |  |  | float | 3 | 2 | 1
24946 | dPF |  |  | float | 3 | 2 | 1
24948 | temperature #1 |  |  | float | 3 | 2 | 1
24950 | temperature #2 |  |  | float | 3 | 2 | 1
24952 | temperature #3 |  |  | float | 3 | 2 | 1
24954 | temperature #4 |  |  | float | 3 | 2 | 1
24956 | temperature #5 |  |  | float | 3 | 2 | 1 | *통신이 끊어진 경우 복구를 위해 사용된다
24958 | Harmonics V1 |  |  | S16 | 3 | 1 | 24
24982 | Harmonics V2 |  |  | S16 | 3 | 1 | 24 | demand
25006 | Harmonics V3 |  |  | S16 | 3 | 1 | 24
25030 | Harmonics V12 |  |  | S16 | 3 | 1 | 24
25054 | Harmonics V23 |  |  | S16 | 3 | 1 | 24
25078 | Harmonics V31 |  |  | S16 | 3 | 1 | 24
25102 | Harmonics I1 |  |  | S16 | 3 | 1 | 24
25126 | Harmonics I2 |  |  | S16 | 3 | 1 | 24
25150 | Harmonics I3 |  |  | S16 | 3 | 1 | 24
25174 |  |  |  | U16 | 3 | 1 | 6
Energy log
25180 | Time Stamp |  |  | UTC | 3 | 2 | 1
25182 | kwh import |  |  | float | 3 | 2 | 1
25184 | kvarh lag |  |  | float | 3 | 2 | 1
25186 | kvarh lead |  |  | float | 3 | 2 | 1
25188 | kVAh |  |  | float | 3 | 2 | 1
25190 | energy log last day 01h |  |  | float | 3 | 2 | 4
25198 | energy log last day 02h |  |  | float | 3 | 2 | 4
25206 | energy log last day 03h |  |  | float | 3 | 2 | 4
25214 | energy log last day 04h |  |  | float | 3 | 2 | 4
25222 | energy log last day 05h |  |  | float | 3 | 2 | 4
25230 | energy log last day 06h |  |  | float | 3 | 2 | 4
25238 | energy log last day 07h |  |  | float | 3 | 2 | 4
25246 | energy log last day 08h |  |  | float | 3 | 2 | 4
25254 | energy log last day 09h |  |  | float | 3 | 2 | 4
25262 | energy log last day 10h |  |  | float | 3 | 2 | 4
25270 | energy log last day 11h |  |  | float | 3 | 2 | 4
25278 | energy log last day 12h |  |  | float | 3 | 2 | 4
25286 | energy log last day 13h |  |  | float | 3 | 2 | 4
25294 | energy log last day 14h |  |  | float | 3 | 2 | 4
25302 | energy log last day 15h |  |  | float | 3 | 2 | 4
25310 | energy log last day 16h |  |  | float | 3 | 2 | 4
25318 | energy log last day 17h |  |  | float | 3 | 2 | 4
25326 | energy log last day 18h |  |  | float | 3 | 2 | 4
25334 | energy log last day 19h |  |  | float | 3 | 2 | 4
25342 | energy log last day 20h |  |  | float | 3 | 2 | 4
25350 | energy log last day 21h |  |  | float | 3 | 2 | 4
25358 | energy log last day 22h |  |  | float | 3 | 2 | 4
25366 | energy log last day 23h |  |  | float | 3 | 2 | 4
25374 |  |  |  | U16 | 3 | 1 | 6
25380 | Time Stamp |  |  | UTC | 3 | 2 | 1
25382 | kwh import |  |  | float | 3 | 2 | 1
25384 | kvarh lag |  |  | float | 3 | 2 | 1
25386 | kvarh lead |  |  | float | 3 | 2 | 1
25388 | kVAh |  |  | float | 3 | 2 | 1
25390 | energy log this day 01h |  |  | float | 3 | 2 | 4
25398 | energy log this day 02h |  |  | float | 3 | 2 | 4
25406 | energy log this day 03h |  |  | float | 3 | 2 | 4
25414 | energy log this day 04h |  |  | float | 3 | 2 | 4
25422 | energy log this day 05h |  |  | float | 3 | 2 | 4
25430 | energy log this day 06h |  |  | float | 3 | 2 | 4
25438 | energy log this day 07h |  |  | float | 3 | 2 | 4
25446 | energy log this day 08h |  |  | float | 3 | 2 | 4
25454 | energy log this day 09h |  |  | float | 3 | 2 | 4
25462 | energy log this day 10h |  |  | float | 3 | 2 | 4
25470 | energy log this day 11h |  |  | float | 3 | 2 | 4
25478 | energy log this day 12h |  |  | float | 3 | 2 | 4
25486 | energy log this day 13h |  |  | float | 3 | 2 | 4
25494 | energy log this day 14h |  |  | float | 3 | 2 | 4 | 전일 디멘트 로그
25502 | energy log this day 15h |  |  | float | 3 | 2 | 4
25510 | energy log this day 16h |  |  | float | 3 | 2 | 4
25518 | energy log this day 17h |  |  | float | 3 | 2 | 4
25526 | energy log this day 18h |  |  | float | 3 | 2 | 4
25534 | energy log this day 19h |  |  | float | 3 | 2 | 4
25542 | energy log this day 20h |  |  | float | 3 | 2 | 4
25550 | energy log this day 21h |  |  | float | 3 | 2 | 4
25558 | energy log this day 22h |  |  | float | 3 | 2 | 4
25566 | energy log this day 23h |  |  | float | 3 | 2 | 4
25574 |  |  |  | U16 | 3 | 1 | 6
demand log last day
25580 | Time Stamp |  |  | U32 | 3 | 2 | 1
25582 | Demand P Array(15분 단위) |  |  | float | 3 | 2 | 96
25774 |  |  |  | U16 | 3 | 1 | 6
ITIC
25780 | fr |  |  | U16 | 3 | 1 | 1
25781 | re |  |  | U16 | 3 | 1 | 1
25782 | count |  |  | U16 | 3 | 1 | 1
25783 | SEQ |  |  | U16 | 3 | 1 | 1
25784 | Log #1 | start ts |  | UTC | 3 | 2 | 1
25786 |  | start ts(ms) |  | U16 | 3 | 1 | 1
25787 |  | duration |  | U16 | 3 | 1 | 1
25788 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
25789 |  | mask |  | U16 | 3 | 1 | 1
25790 |  | Level 1 |  | float | 3 | 2 | 1
25792 |  | Level 2 |  | float | 3 | 2 | 1
25794 |  | Level 3 |  | float | 3 | 2 | 1
25796 |  | Normal |  | float | 3 | 2 | 1
25798 | Log #2 |  |  | U16 | 3 | 1 | 14
25812 | Log #3 |  |  | U16 | 3 | 1 | 14
25826 | Log #4 |  |  | U16 | 3 | 1 | 14
25840 | Log #5 |  |  | U16 | 3 | 1 | 14
25854 | Log #6 |  |  | U16 | 3 | 1 | 14
25868 | Log #7 |  |  | U16 | 3 | 1 | 14
25882 | Log #8 |  |  | U16 | 3 | 1 | 14
25896 | Log #9 |  |  | U16 | 3 | 1 | 14
25910 | Log #10 |  |  | U16 | 3 | 1 | 14
25924 | Log #11 |  |  | U16 | 3 | 1 | 14
25938 | Log #12 |  |  | U16 | 3 | 1 | 14
25952 | Log #13 |  |  | U16 | 3 | 1 | 14
25966 | Log #14 |  |  | U16 | 3 | 1 | 14
25980 | Log #15 |  |  | U16 | 3 | 1 | 14
25994 | Log #16 |  |  | U16 | 3 | 1 | 14
26008 | Log #17 |  |  | U16 | 3 | 1 | 14
26022 | Log #18 |  |  | U16 | 3 | 1 | 14
26036 | Log #19 |  |  | U16 | 3 | 1 | 14
26050 | Log #20 |  |  | U16 | 3 | 1 | 14
26064 | Log #21 |  |  | U16 | 3 | 1 | 14
26078 | Log #22 |  |  | U16 | 3 | 1 | 14
26092 | Log #23 |  |  | U16 | 3 | 1 | 14
26106 | Log #24 |  |  | U16 | 3 | 1 | 14
26120 | Log #25 |  |  | U16 | 3 | 1 | 14
26134 | Log #26 |  |  | U16 | 3 | 1 | 14
26148 | Log #27 |  |  | U16 | 3 | 1 | 14
26162 | Log #28 |  |  | U16 | 3 | 1 | 14
26176 | Log #29 |  |  | U16 | 3 | 1 | 14
26190 | Log #30 |  |  | U16 | 3 | 1 | 14
26204 | Log #31 |  |  | U16 | 3 | 1 | 14
26218 | Log #32 |  |  | U16 | 3 | 1 | 14
26232 |  |  |  | U16 | 3 | 1 | 8
ITIC(Configurator)
26240 | fr |  |  | U16 | 3 | 1 | 1
26241 | re |  |  | U16 | 3 | 1 | 1
26242 | count |  |  | U16 | 3 | 1 | 1
26243 | reserved |  |  | U16 | 3 | 1 | 1
26244 | Log #1 | start ts |  | UTC | 3 | 2 | 1
26246 |  | start ts(ms) |  | U16 | 3 | 1 | 1
26247 |  | duration |  | U16 | 3 | 1 | 1
26248 |  | type | #define E_SAG 1 #define E_SWELL 2 #define E_sINTR 3 #define E_lINTR 4 #define E_OC 5 #define E_RVC 6 #define E_TrV 7 #define E_TrC 8 bit15: 1 -> Event Only | U16 | 3 | 1 | 1
26249 |  | mask |  | U16 | 3 | 1 | 1
26250 |  | Level 1 |  | float | 3 | 2 | 1
26252 |  | Level 2 |  | float | 3 | 2 | 1
26254 |  | Level 3 |  | float | 3 | 2 | 1
26256 |  | Normal |  | float | 3 | 2 | 1
26258 | Log #2 |  |  | U16 | 3 | 1 | 14
26272 | Log #3 |  |  | U16 | 3 | 1 | 14
26286 | Log #4 |  |  | U16 | 3 | 1 | 14
26300 | Log #5 |  |  | U16 | 3 | 1 | 14
26314 | Log #6 |  |  | U16 | 3 | 1 | 14
26328 | Log #7 |  |  | U16 | 3 | 1 | 14
26342 | Log #8 |  |  | U16 | 3 | 1 | 14
26356 | Log #9 |  |  | U16 | 3 | 1 | 14
26370 | Log #10 |  |  | U16 | 3 | 1 | 14
26384 | Log #11 |  |  | U16 | 3 | 1 | 14
26398 | Log #12 |  |  | U16 | 3 | 1 | 14
26412 | Log #13 |  |  | U16 | 3 | 1 | 14
26426 | Log #14 |  |  | U16 | 3 | 1 | 14
26440 | Log #15 |  |  | U16 | 3 | 1 | 14
26454 | Log #16 |  |  | U16 | 3 | 1 | 14
26468 | Log #17 |  |  | U16 | 3 | 1 | 14
26482 | Log #18 |  |  | U16 | 3 | 1 | 14
26496 | Log #19 |  |  | U16 | 3 | 1 | 14
26510 | Log #20 |  |  | U16 | 3 | 1 | 14
26524 | Log #21 |  |  | U16 | 3 | 1 | 14
26538 | Log #22 |  |  | U16 | 3 | 1 | 14
26552 | Log #23 |  |  | U16 | 3 | 1 | 14
26566 | Log #24 |  |  | U16 | 3 | 1 | 14
26580 | Log #25 |  |  | U16 | 3 | 1 | 14
26594 | Log #26 |  |  | U16 | 3 | 1 | 14
26608 | Log #27 |  |  | U16 | 3 | 1 | 14
26622 | Log #28 |  |  | U16 | 3 | 1 | 14
26636 | Log #29 |  |  | U16 | 3 | 1 | 14
26650 | Log #30 |  |  | U16 | 3 | 1 | 14
26664 | Log #31 |  |  | U16 | 3 | 1 | 14
26678 | Log #32 |  |  | U16 | 3 | 1 | 14
26692 |  |  |  | U16 | 3 | 1 | 8
Setting 영역 시작
PQ Event
26700 | OC Level | 정격의 2배 |  | U16 | 3,16 | 1 | 1
26701 | OC Cycle | unused |  | U16 | 3,16 | 1 | 1
26702 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
26703 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
26704 |  |  |  | U16 | 3,16 | 1 | 2
26706 | Sag Level(%), 90% | < 90% |  | U16 | 3,16 | 1 | 1
26707 | Sag Cycle | unused |  | U16 | 3,16 | 1 | 1
26708 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
26709 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
26710 |  |  |  | U16 | 3,16 | 1 | 2
26712 | Swell Level(%), 110~200~ | > 110% |  | U16 | 3,16 | 1 | 1
26713 | Swell Cycle | unused |  | U16 | 3,16 | 1 | 1
26714 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
26715 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
26716 |  |  |  | U16 | 3,16 | 1 | 2
26718 | Interruption Level, 5% | < 5% |  | U16 | 3,16 | 1 | 1
26719 | Interruption Time, 60s | unused |  | U16 | 3,16 | 1 | 1
26720 | Trigger Action | 0: None 1: Event Only, 2: Wave Capture&RMS |  | U16 | 3,16 | 1 | 1
26721 | holdOff Cycle |  |  | U16 | 3,16 | 1 | 1
26722 |  |  |  | U16 | 3,16 | 1 | 2
Transient Trigger
26724 | Transient Voltage, HoldOff Time, 20ms | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
26725 | Transient Voltage, Absolute Peak Level, 200% | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
26726 | Transient Voltage, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
26727 | Transient Voltage, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
26728 | Transient Current, HoldOff Time | 200 ~ 1000ms |  | U16 | 3,16 | 1 | 1
26729 | Transient Current, Absolute Peak Level | 120 ~ 300% |  | U16 | 3,16 | 1 | 1
26730 | Transient Current, Fast Change(%U/us) | 4~10% (120 ~ 320%) |  | U16 | 3,16 | 1 | 1
26731 | Transient Current, Trigger Action | 0: None 1: Event Only, 2: Wave Capture |  | U16 | 3,16 | 1 | 1
26732 |  |  |  | U16 | 3,16 | 1 | 12
Recorder
Waveform
26744 | Recorder resolution(32k, 8k) |  |  | U16 | 3,16 | 1 | 1
26745 | Recorded paramater (U or I) |  |  | U16 | 3,16 | 1 | 1
26746 | pre trigger time(0.1s) |  |  | U16 | 3,16 | 1 | 1
26747 | post trigger time(1s) |  |  | U16 | 3,16 | 1 | 1
Disturbance
26748 | Recorder resolution (Half Cycle) |  |  | U16 | 3,16 | 1 | 1
26749 | Recorded parametrs(U or I) |  |  | U16 | 3,16 | 1 | 1
26750 | pre trigger time(100 sample) |  |  | U16 | 3,16 | 1 | 1
26751 | post trigger time(900 sample) |  |  | U16 | 3,16 | 1 | 1
26752 |  |  |  | U16 | 3,16 | 1 | 12
Trend Recorder
26764 | Trend Group #1 Active |  |  | U16 | 3,16 | 1 | 1
26765 | Trend Group #1 Storage Interval |  |  | U16 | 3,16 | 1 | 1
26766 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
26767 | Trend Group #1, Channel #1 |  |  | U16 | 3,16 | 1 | 1
26768 | Trend Group #1, Channel #2 |  |  | U16 | 3,16 | 1 | 1
26769 | Trend Group #1, Channel #3 |  |  | U16 | 3,16 | 1 | 1
26770 | Trend Group #1, Channel #4 |  |  | U16 | 3,16 | 1 | 1
26771 | Trend Group #1, Channel #5 |  |  | U16 | 3,16 | 1 | 1
26772 | Trend Group #1, Channel #6 |  |  | U16 | 3,16 | 1 | 1
26773 | Trend Group #1, Channel #7 |  |  | U16 | 3,16 | 1 | 1
26774 | Trend Group #1, Channel #8 |  |  | U16 | 3,16 | 1 | 1
26775 | Trend Group #1, Channel #9 |  |  | U16 | 3,16 | 1 | 1
26776 | Trend Group #1, Channel #10 |  |  | U16 | 3,16 | 1 | 1
26777 | Trend Group #1, Channel #11 |  |  | U16 | 3,16 | 1 | 1
26778 | Trend Group #1, Channel #12 |  |  | U16 | 3,16 | 1 | 1
26779 | Trend Group #1, Channel #13 |  |  | U16 | 3,16 | 1 | 1
26780 | Trend Group #1, Channel #14 |  |  | U16 | 3,16 | 1 | 1
26781 | Trend Group #1, Channel #15 |  |  | U16 | 3,16 | 1 | 1
26782 | Trend Group #1, Channel #16 |  |  | U16 | 3,16 | 1 | 1
26783 | Trend Group #2 Active |  |  | U16 | 3,16 | 1 | 1
26784 | Trend Group #2 Storage Interval |  |  | U16 | 3,16 | 1 | 1
26785 | Trend Group #1 Version |  |  | U16 | 3,16 | 1 | 1
26786 | Trend Group #2, Channel #1 |  |  | U16 | 3,16 | 1 | 1
26787 | Trend Group #2, Channel #2 |  |  | U16 | 3,16 | 1 | 1
26788 | Trend Group #2, Channel #3 |  |  | U16 | 3,16 | 1 | 1
26789 | Trend Group #2, Channel #4 |  |  | U16 | 3,16 | 1 | 1
26790 | Trend Group #2, Channel #5 |  |  | U16 | 3,16 | 1 | 1
26791 | Trend Group #2, Channel #6 |  |  | U16 | 3,16 | 1 | 1
26792 | Trend Group #2, Channel #7 |  |  | U16 | 3,16 | 1 | 1
26793 | Trend Group #2, Channel #8 |  |  | U16 | 3,16 | 1 | 1
26794 | Trend Group #2, Channel #9 |  |  | U16 | 3,16 | 1 | 1
26795 | Trend Group #2, Channel #10 |  |  | U16 | 3,16 | 1 | 1
26796 | Trend Group #2, Channel #11 |  |  | U16 | 3,16 | 1 | 1
26797 | Trend Group #2, Channel #12 |  |  | U16 | 3,16 | 1 | 1
26798 | Trend Group #2, Channel #13 |  |  | U16 | 3,16 | 1 | 1
26799 | Trend Group #2, Channel #14 |  |  | U16 | 3,16 | 1 | 1
26800 | Trend Group #2, Channel #15 |  |  | U16 | 3,16 | 1 | 1
26801 | Trend Group #2, Channel #16 |  |  | U16 | 3,16 | 1 | 1
26802 | Trend Group #3 Active |  |  | U16 | 3,16 | 1 | 1
26803 | Trend Group #3 Storage Interval |  |  | U16 | 3,16 | 1 | 1
26804 |  |  |  | U16 | 3,16 | 1 | 1
26805 | Trend Group #3, Channel #1 |  |  | U16 | 3,16 | 1 | 1
26806 | Trend Group #3, Channel #2 |  |  | U16 | 3,16 | 1 | 1
26807 | Trend Group #3, Channel #3 |  |  | U16 | 3,16 | 1 | 1
26808 | Trend Group #3, Channel #4 |  |  | U16 | 3,16 | 1 | 1
26809 | Trend Group #3, Channel #5 |  |  | U16 | 3,16 | 1 | 1
26810 | Trend Group #3, Channel #6 |  |  | U16 | 3,16 | 1 | 1
26811 | Trend Group #3, Channel #7 |  |  | U16 | 3,16 | 1 | 1
26812 | Trend Group #3, Channel #8 |  |  | U16 | 3,16 | 1 | 1
26813 | Trend Group #3, Channel #9 |  |  | U16 | 3,16 | 1 | 1
26814 | Trend Group #3, Channel #10 |  |  | U16 | 3,16 | 1 | 1
26815 | Trend Group #3, Channel #11 |  |  | U16 | 3,16 | 1 | 1
26816 | Trend Group #3, Channel #12 |  |  | U16 | 3,16 | 1 | 1
26817 | Trend Group #3, Channel #13 |  |  | U16 | 3,16 | 1 | 1
26818 | Trend Group #3, Channel #14 |  |  | U16 | 3,16 | 1 | 1
26819 | Trend Group #3, Channel #15 |  |  | U16 | 3,16 | 1 | 1
26820 | Trend Group #3, Channel #16 |  |  | U16 | 3,16 | 1 | 1
26821 | Trend Group #4 Active |  |  | U16 | 3,16 | 1 | 1
26822 | Trend Group #4 Storage Interval |  |  | U16 | 3,16 | 1 | 1
26823 |  |  |  | U16 | 3,16 | 1 | 1
26824 | Trend Group #4, Channel #1 |  |  | U16 | 3,16 | 1 | 1
26825 | Trend Group #4, Channel #2 |  |  | U16 | 3,16 | 1 | 1
26826 | Trend Group #4, Channel #3 |  |  | U16 | 3,16 | 1 | 1
26827 | Trend Group #4, Channel #4 |  |  | U16 | 3,16 | 1 | 1
26828 | Trend Group #4, Channel #5 |  |  | U16 | 3,16 | 1 | 1
26829 | Trend Group #4, Channel #6 |  |  | U16 | 3,16 | 1 | 1
26830 | Trend Group #4, Channel #7 |  |  | U16 | 3,16 | 1 | 1
26831 | Trend Group #4, Channel #8 |  |  | U16 | 3,16 | 1 | 1
26832 | Trend Group #4, Channel #9 |  |  | U16 | 3,16 | 1 | 1
26833 | Trend Group #4, Channel #10 |  |  | U16 | 3,16 | 1 | 1
26834 | Trend Group #4, Channel #11 |  |  | U16 | 3,16 | 1 | 1
26835 | Trend Group #4, Channel #12 |  |  | U16 | 3,16 | 1 | 1
26836 | Trend Group #4, Channel #13 |  |  | U16 | 3,16 | 1 | 1
26837 | Trend Group #4, Channel #14 |  |  | U16 | 3,16 | 1 | 1
26838 | Trend Group #4, Channel #15 |  |  | U16 | 3,16 | 1 | 1
26839 | Trend Group #4, Channel #16 |  |  | U16 | 3,16 | 1 | 1
26840 |  |  |  | U16 | 3,16 | 1 | 4
Power Quality Report
26844 | Active |  |  | U16 | 3,16 | 1 | 1
26845 | Start Day |  |  | U16 | 3,16 | 1 | 1
26846 |  |  |  | U16 |  | 1 | 8
Alarm Definition
26854 | compare Time Delay(1s) |  |  | U16 | 3,16 | 1 | 1
26855 |  |  |  | U16 |  | 1 | 1
26856 |  |  |  | U16 |  | 1 | 1
26857 |  |  |  | U16 |  | 1 | 1
Alarm Settings
26858 | Alarm Info #1 Channel(0:disabled, >0: enabled) |  |  | U16 | 3,16 | 1 | 1
26859 | Alarm Cond (0: < , 1:>) |  |  | U16 | 3,16 | 1 | 1
26860 | Hysteresis (% of Nominal) |  |  | U16 | 3,16 | 1 | 1
26861 | Alarm Action (None, Relay or Beep) |  |  | U16 | 3,16 | 1 | 1
26862 | Alarm Level |  |  | float | 3,16 | 2 | 1
26864 | Alarm Settings #2 |  |  | U16 | 3,16 | 1 | 6
26870 | Alarm Settings #3 |  |  | U16 | 3,16 | 1 | 6
26876 | Alarm Settings #4 |  |  | U16 | 3,16 | 1 | 6
26882 | Alarm Settings #5 |  |  | U16 | 3,16 | 1 | 6
26888 | Alarm Settings #6 |  |  | U16 | 3,16 | 1 | 6
26894 | Alarm Settings #7 |  |  | U16 | 3,16 | 1 | 6
26900 | Alarm Settings #8 |  |  | U16 | 3,16 | 1 | 6
26906 | Alarm Settings #9 |  |  | U16 | 3,16 | 1 | 6
26912 | Alarm Settings #10 |  |  | U16 | 3,16 | 1 | 6
26918 | Alarm Settings #11 |  |  | U16 | 3,16 | 1 | 6
26924 | Alarm Settings #12 |  |  | U16 | 3,16 | 1 | 6
26930 | Alarm Settings #13 |  |  | U16 | 3,16 | 1 | 6
26936 | Alarm Settings #14 |  |  | U16 | 3,16 | 1 | 6
26942 | Alarm Settings #15 |  |  | U16 | 3,16 | 1 | 6
26948 | Alarm Settings #16 |  |  | U16 | 3,16 | 1 | 6
26954 | Alarm Settings #17 |  |  | U16 | 3,16 | 1 | 6
26960 | Alarm Settings #18 |  |  | U16 | 3,16 | 1 | 6
26966 | Alarm Settings #19 |  |  | U16 | 3,16 | 1 | 6
26972 | Alarm Settings #20 |  |  | U16 | 3,16 | 1 | 6
26978 | Alarm Settings #21 |  |  | U16 | 3,16 | 1 | 6
26984 | Alarm Settings #22 |  |  | U16 | 3,16 | 1 | 6
26990 | Alarm Settings #23 |  |  | U16 | 3,16 | 1 | 6
26996 | Alarm Settings #24 |  |  | U16 | 3,16 | 1 | 6
27002 | Alarm Settings #25 |  |  | U16 | 3,16 | 1 | 6
27008 | Alarm Settings #26 |  |  | U16 | 3,16 | 1 | 6
27014 | Alarm Settings #27 |  |  | U16 | 3,16 | 1 | 6
27020 | Alarm Settings #28 |  |  | U16 | 3,16 | 1 | 6
27026 | Alarm Settings #29 |  |  | U16 | 3,16 | 1 | 6
27032 | Alarm Settings #30 |  |  | U16 | 3,16 | 1 | 6
27038 | Alarm Settings #31 |  |  | U16 | 3,16 | 1 | 6
27044 | Alarm Settings #32 |  |  | U16 | 3,16 | 1 | 6
27050

## Alarm Channel
Trend/Alarm Channel
1 | Temp
2 | Freq
3 | U1
4 | U2
5 | U3
6 | U~
7 | U12
8 | U23
9 | U31
10 | Upp~
11 | Voltage Unbalace, Uo
12 | Voltage Unbalace, Uu
13 | I1
14 | I2
15 | I3
16 | I~
17 | Itotal
18 | In
19 | P1
20 | P2
21 | P3
22 | Ptotal
23 | Q1
24 | Q2
25 | Q3
26 | Qtot
27 | D1
28 | D2
29 | D3
30 | D
31 | S1
32 | S2
33 | S3
34 | Stot
35 | PF1
36 | PF2
37 | PF3
38 | PFtot
39 | THD U1
40 | THD U2
41 | THD U3
42 | THD U12
43 | THD U23
44 | THD U31
45 | THD I1
46 | THD I2
47 | THD I3
48 | Dynamic Demand P+
49 | Dynamic Demand P-
50 | Dynamic Demand Q+
51 | Dynamic Demand Q-
52 | Dynamic Demand S
53 | Dynamic Demand I1
54 | Dynamic Demand I2
55 | Dynamic Demand I3
56 | Max. Demand P+
57 | Max. Demand P=-
58 | Max. Demand Q+
59 | Max. Demand Q-
60 | Max. Demand S
61 | Max. Demand I1
62 | Max. Demand I2
63 | Max. Demand I3
64 | Under Deviation U1
65 | Under Deviation U2
66 | Under Deviation U3
67 | Over Drviation U1
68 | Over Drviation U2
69 | Over Drviation U3
70 | CF U1
71 | CF U2
72 | CF U3
73 | CF U12
74 | CF U23
75 | CF U31
76 | CF I1
77 | CF I2
78 | CF I3
79 | KF I1
80 | KF I2
81 | KF I3
82 | PSt 1
83 | PSt 2
84 | PSt 3
85 | Plt 1
86 | Plt 2
87 | Plt 3
88 | Sig. Volt 1
89 | Sig. Volt 2
90 | Sig. Volt 3